## Summary
Summary
This spreadsheet provides example Modbus maps implemented in the Multi-Stack Controller product from Nuvation Energy
Each spreadsheet tab is an example map sized for a maximum possible size of a system:
Sheet Name | Maximum Stacks | Maximum Cell Interfaces | Maximum Cells
Sample_Map_2Stack_4CI_24Cell | 2 | 4 | 24
Sample_Map_4Stack_18CI_16Cell | 4 | 18 | 16
Bitfields and Enums | - | - | -
The column descriptions for each are below:
Offset | Modbus register address
Model | SunSpec Model String Label
Model Label | SunSpec Model Description
Name | SunSpec Point Name
Description | SunSpec Point Description
Type | SunSpec Point Data Type
Group | SunSpec Model Repeating Block String Label
Mandatory | SunSpec Mandatory Point (TRUE/FALSE)
Implemented | Multi-Stack Controller Implemented Point (TRUE/FALSE)
Bit Name | Individual Bit Name for Bitfield/Enum Points
SunSpec 'string' is equivalent to 'stack'
SunSpec 'module' is equivalent to 'cell interface'
NOTE: these are provided as examples and the final map will depend on the maximums of a site.
Consult the Nuvation Energy Technical Resources page for more details.
Contact Nuvation Support for questions or concerns.
Revision | Description
1.1 | Add enum/bitfield Definition sheet
1.0 | Initial release for MSC 21.0.0-21.2.0
0.1 | Initial draft for MSC 21.0.0-21.1.0
Copyright Nuvation Energy 2024. All Rights Reserved.
This material is provided 'as-is' and comes with neither express warranties nor implied warranties. Nuvation Energy is not liable for any damages sustained by the use of this material. Please use at your own risk.

## Sample_Map_2Stack_4CI_24Cell
Offset | Model | Model Label | Name | Description | Type | Group | Mandatory | Implemented
0 | Start | start | mmid_hi | Model map identifier hi | uint16 |  | TRUE | TRUE
1 | Start | start | mmid_lo | Model map identifier lo | uint16 |  | TRUE | TRUE
2 | common | Common | ID | Model identifier | uint16 |  | TRUE | TRUE
3 | common | Common | L | Model length | uint16 |  | TRUE | TRUE
4 | common | Common | Mn | Well known value registered with SunSpec for compliance | string |  | TRUE | TRUE
20 | common | Common | Md | Manufacturer specific value (32 chars) | string |  | TRUE | TRUE
36 | common | Common | Opt | Manufacturer specific value (16 chars) | string |  | FALSE | TRUE
44 | common | Common | Vr | Manufacturer specific value (16 chars) | string |  | FALSE | TRUE
52 | common | Common | SN | Manufacturer specific value (32 chars) | string |  | TRUE | TRUE
68 | common | Common | DA | Modbus device address | uint16 |  | FALSE | TRUE
69 | common | Common | Pad | Force even alignment | pad |  | FALSE | TRUE
70 | battery | Battery Base Model | ID | Model identifier | uint16 |  | TRUE | TRUE
71 | battery | Battery Base Model | L | Model length | uint16 |  | TRUE | TRUE
72 | battery | Battery Base Model | AHRtg | Nameplate charge capacity in amp-hours. | uint16 |  | TRUE | TRUE
73 | battery | Battery Base Model | WHRtg | Nameplate energy capacity in DC watt-hours. | uint16 |  | TRUE | TRUE
74 | battery | Battery Base Model | WChaRteMax | Maximum rate of energy transfer into the storage device in DC watts. | uint16 |  | TRUE | TRUE
75 | battery | Battery Base Model | WDisChaRteMax | Maximum rate of energy transfer out of the storage device in DC watts. | uint16 |  | TRUE | TRUE
76 | battery | Battery Base Model | DisChaRte | Self discharge rate. Percentage of capacity (WHRtg) discharged per day. | uint16 |  | FALSE | FALSE
77 | battery | Battery Base Model | SoCMax | Manufacturer maximum state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
78 | battery | Battery Base Model | SoCMin | Manufacturer minimum state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
79 | battery | Battery Base Model | SocRsvMax | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage. | uint16 |  | FALSE | FALSE
80 | battery | Battery Base Model | SoCRsvMin | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage. | uint16 |  | FALSE | FALSE
81 | battery | Battery Base Model | SoC | State of charge, expressed as a percentage. | uint16 |  | TRUE | TRUE
82 | battery | Battery Base Model | DoD | Depth of discharge, expressed as a percentage. | uint16 |  | FALSE | FALSE
83 | battery | Battery Base Model | SoH | Percentage of battery life remaining. | uint16 |  | FALSE | TRUE
84 | battery | Battery Base Model | NCyc | Number of cycles executed in the battery. | uint32 |  | FALSE | FALSE
86 | battery | Battery Base Model | ChaSt | Charge status of storage device. Enumeration. | enum16 |  | FALSE | FALSE
87 | battery | Battery Base Model | LocRemCtl | Battery control mode. Enumeration. | enum16 |  | TRUE | TRUE
88 | battery | Battery Base Model | Hb | Value is incremented every second with periodic resets to zero. | uint16 |  | FALSE | TRUE
89 | battery | Battery Base Model | CtrlHb | Value is incremented every second with periodic resets to zero. | uint16 |  | FALSE | TRUE
90 | battery | Battery Base Model | AlmRst | Used to reset any latched alarms. 1 = Reset. | uint16 |  | TRUE | TRUE
91 | battery | Battery Base Model | Typ | Type of battery. Enumeration. | enum16 |  | TRUE | TRUE
92 | battery | Battery Base Model | State | State of the battery bank. Enumeration. | enum16 |  | TRUE | TRUE
93 | battery | Battery Base Model | StateVnd | Vendor specific battery bank state. Enumeration. | enum16 |  | FALSE | FALSE
94 | battery | Battery Base Model | WarrDt | Date the device warranty expires. | uint32 |  | FALSE | FALSE
96 | battery | Battery Base Model | Evt1 | Alarms and warnings. Bit flags. | bitfield32 |  | TRUE | TRUE
98 | battery | Battery Base Model | Evt2 | Alarms and warnings. Bit flags. | bitfield32 |  | TRUE | TRUE
100 | battery | Battery Base Model | EvtVnd1 | Vendor defined events. | bitfield32 |  | TRUE | TRUE
102 | battery | Battery Base Model | EvtVnd2 | Vendor defined events. | bitfield32 |  | TRUE | TRUE
104 | battery | Battery Base Model | V | DC Bus Voltage. | uint16 |  | TRUE | TRUE
105 | battery | Battery Base Model | VMax | Instantaneous maximum battery voltage. | uint16 |  | FALSE | FALSE
106 | battery | Battery Base Model | VMin | Instantaneous minimum battery voltage. | uint16 |  | FALSE | FALSE
107 | battery | Battery Base Model | CellVMax | Maximum voltage for all cells in the bank. | uint16 |  | FALSE | TRUE
108 | battery | Battery Base Model | CellVMaxStr | String containing the cell with maximum voltage. | uint16 |  | FALSE | TRUE
109 | battery | Battery Base Model | CellVMaxMod | Module containing the cell with maximum voltage. | uint16 |  | FALSE | FALSE
110 | battery | Battery Base Model | CellVMin | Minimum voltage for all cells in the bank. | uint16 |  | FALSE | TRUE
111 | battery | Battery Base Model | CellVMinStr | String containing the cell with minimum voltage. | uint16 |  | FALSE | TRUE
112 | battery | Battery Base Model | CellVMinMod | Module containing the cell with minimum voltage. | uint16 |  | FALSE | TRUE
113 | battery | Battery Base Model | CellVAvg | Average cell voltage for all cells in the bank. | uint16 |  | FALSE | TRUE
114 | battery | Battery Base Model | A | Total DC current flowing to/from the battery bank. | int16 |  | TRUE | TRUE
115 | battery | Battery Base Model | AChaMax | Instantaneous maximum DC charge current. | uint16 |  | FALSE | TRUE
116 | battery | Battery Base Model | ADisChaMax | Instantaneous maximum DC discharge current. | uint16 |  | FALSE | TRUE
117 | battery | Battery Base Model | W | Total power flowing to/from the battery bank. | int16 |  | TRUE | TRUE
118 | battery | Battery Base Model | ReqInvState | Request from battery to start or stop the inverter. Enumeration. | enum16 |  | FALSE | FALSE
119 | battery | Battery Base Model | ReqW | AC Power requested by battery. | int16 |  | FALSE | FALSE
120 | battery | Battery Base Model | SetOp | Instruct the battery bank to perform an operation such as connecting. Enumeration. | enum16 |  | TRUE | TRUE
121 | battery | Battery Base Model | SetInvState | Set the current state of the inverter. | enum16 |  | TRUE | TRUE
122 | battery | Battery Base Model | AHRtg_SF | Scale factor for charge capacity. | sunssf |  | TRUE | TRUE
123 | battery | Battery Base Model | WHRtg_SF | Scale factor for energy capacity. | sunssf |  | TRUE | TRUE
124 | battery | Battery Base Model | WChaDisChaMax_SF | Scale factor for maximum charge and discharge rate. | sunssf |  | TRUE | TRUE
125 | battery | Battery Base Model | DisChaRte_SF | Scale factor for self discharge rate. | sunssf |  | FALSE | FALSE
126 | battery | Battery Base Model | SoC_SF | Scale factor for state of charge values. | sunssf |  | TRUE | TRUE
127 | battery | Battery Base Model | DoD_SF | Scale factor for depth of discharge. | sunssf |  | FALSE | FALSE
128 | battery | Battery Base Model | SoH_SF | Scale factor for state of health. | sunssf |  | FALSE | TRUE
129 | battery | Battery Base Model | V_SF | Scale factor for DC bus voltage. | sunssf |  | TRUE | TRUE
130 | battery | Battery Base Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
131 | battery | Battery Base Model | A_SF | Scale factor for DC current. | sunssf |  | TRUE | TRUE
132 | battery | Battery Base Model | AMax_SF | Scale factor for instantaneous DC charge/discharge current. | sunssf |  | TRUE | TRUE
133 | battery | Battery Base Model | W_SF | Scale factor for AC power request. | sunssf |  | FALSE | TRUE
134 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ID | Model identifier | uint16 |  | TRUE | TRUE
135 | lithium_ion_bank | Lithium-Ion Battery Bank Model | L | Model length | uint16 |  | TRUE | TRUE
136 | lithium_ion_bank | Lithium-Ion Battery Bank Model | NStr | Number of strings in the bank. | uint16 |  | TRUE | TRUE
137 | lithium_ion_bank | Lithium-Ion Battery Bank Model | NStrCon | Number of strings with contactor closed. | uint16 |  | TRUE | TRUE
138 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpMax | Maximum temperature for all modules in the bank. | int16 |  | TRUE | TRUE
139 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpMaxStr | String containing the module with maximum temperature. | uint16 |  | FALSE | TRUE
140 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpMaxMod | Module with maximum temperature. | uint16 |  | FALSE | TRUE
141 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpMin | Minimum temperature for all modules in the bank. | int16 |  | TRUE | TRUE
142 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpMinStr | String containing the module with minimum temperature. | uint16 |  | FALSE | TRUE
143 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpMinMod | Module with minimum temperature. | uint16 |  | FALSE | TRUE
144 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpAvg | Average temperature for all modules in the bank. | int16 |  | FALSE | TRUE
145 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrVMax | Maximum string voltage for all strings in the bank. | uint16 |  | FALSE | TRUE
146 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrVMaxStr | String with maximum voltage. | uint16 |  | FALSE | FALSE
147 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrVMin | Minimum string voltage for all strings in the bank. | uint16 |  | FALSE | TRUE
148 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrVMinStr | String with minimum voltage. | uint16 |  | FALSE | FALSE
149 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrVAvg | Average string voltage for all strings in the bank. | uint16 |  | FALSE | TRUE
150 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrAMax | Maximum current of any string in the bank. | int16 |  | FALSE | TRUE
151 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrAMaxStr | String with the maximum current. | uint16 |  | FALSE | FALSE
152 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrAMin | Minimum current of any string in the bank. | int16 |  | FALSE | TRUE
153 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrAMinStr | String with the minimum current. | uint16 |  | FALSE | FALSE
154 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrAAvg | Average string current for all strings in the bank. | int16 |  | FALSE | TRUE
155 | lithium_ion_bank | Lithium-Ion Battery Bank Model | NCellBal | Total number of cells that are currently being balanced. | uint16 |  | FALSE | FALSE
156 | lithium_ion_bank | Lithium-Ion Battery Bank Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
157 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmp_SF | Scale factor for module temperatures. | sunssf |  | TRUE | TRUE
158 | lithium_ion_bank | Lithium-Ion Battery Bank Model | A_SF | Scale factor for string currents. | sunssf |  | TRUE | TRUE
159 | lithium_ion_bank | Lithium-Ion Battery Bank Model | SoH_SF | Scale factor for string state of health. | sunssf |  | FALSE | TRUE
160 | lithium_ion_bank | Lithium-Ion Battery Bank Model | SoC_SF | Scale factor for string state of charge. | sunssf |  | TRUE | TRUE
161 | lithium_ion_bank | Lithium-Ion Battery Bank Model | V_SF | Scale factor for string voltage. | sunssf |  | FALSE | TRUE
162 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrNMod | Count of modules in the string. | uint16 | string.0 | TRUE | TRUE
163 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSt | Current status of the string. | bitfield32 | string.0 | TRUE | TRUE
165 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrConFail |  | enum16 | string.0 | FALSE | FALSE
166 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSoC | Battery string state of charge, expressed as a percentage. | uint16 | string.0 | TRUE | TRUE
167 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSoH | Battery string state of health, expressed as a percentage. | uint16 | string.0 | FALSE | TRUE
168 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrA | String current measurement. | int16 | string.0 | TRUE | TRUE
169 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMax | Maximum voltage for all cells in the string. | uint16 | string.0 | TRUE | TRUE
170 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMaxMod | Module containing the maximum cell voltage. | uint16 | string.0 | FALSE | TRUE
171 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMin | Minimum voltage for all cells in the string. | uint16 | string.0 | TRUE | TRUE
172 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMinMod | Module containing the minimum cell voltage. | uint16 | string.0 | FALSE | TRUE
173 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVAvg | Average voltage for all cells in the string. | uint16 | string.0 | TRUE | TRUE
174 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMax | Maximum temperature for all modules in the bank. | int16 | string.0 | TRUE | TRUE
175 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMaxMod | Module with the maximum temperature. | uint16 | string.0 | FALSE | TRUE
176 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMin | Minimum temperature for all modules in the bank. | int16 | string.0 | TRUE | TRUE
177 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMinMod | Module with the minimum temperature. | uint16 | string.0 | FALSE | TRUE
178 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpAvg | Average temperature for all modules in the bank. | int16 | string.0 | TRUE | TRUE
179 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrDisRsn | Reason why the string is currently disabled. | enum16 | string.0 | FALSE | FALSE
180 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrConSt | Status of the contactor(s) for the string. | bitfield32 | string.0 | FALSE | FALSE
182 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | Alarms, warnings and status values. Bit flags. | bitfield32 | string.0 | TRUE | TRUE
184 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt2 | Alarms, warnings and status values. Bit flags. | bitfield32 | string.0 | FALSE | FALSE
186 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvtVnd1 | Vendor defined events. | bitfield32 | string.0 | FALSE | FALSE
188 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvtVnd2 | Vendor defined events. | bitfield32 | string.0 | FALSE | FALSE
190 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetEna | Enables and disables the string. | enum16 | string.0 | FALSE | TRUE
191 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetCon | Connects and disconnects the string. | enum16 | string.0 | FALSE | TRUE
192 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.Pad1 | Pad register. | pad | string.0 | TRUE | TRUE
193 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.Pad2 | Pad register. | pad | string.0 | TRUE | TRUE
194 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrNMod | Count of modules in the string. | uint16 | string.1 | TRUE | TRUE
195 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSt | Current status of the string. | bitfield32 | string.1 | TRUE | TRUE
197 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrConFail |  | enum16 | string.1 | FALSE | FALSE
198 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSoC | Battery string state of charge, expressed as a percentage. | uint16 | string.1 | TRUE | TRUE
199 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSoH | Battery string state of health, expressed as a percentage. | uint16 | string.1 | FALSE | TRUE
200 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrA | String current measurement. | int16 | string.1 | TRUE | TRUE
201 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMax | Maximum voltage for all cells in the string. | uint16 | string.1 | TRUE | TRUE
202 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMaxMod | Module containing the maximum cell voltage. | uint16 | string.1 | FALSE | TRUE
203 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMin | Minimum voltage for all cells in the string. | uint16 | string.1 | TRUE | TRUE
204 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMinMod | Module containing the minimum cell voltage. | uint16 | string.1 | FALSE | TRUE
205 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVAvg | Average voltage for all cells in the string. | uint16 | string.1 | TRUE | TRUE
206 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMax | Maximum temperature for all modules in the bank. | int16 | string.1 | TRUE | TRUE
207 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMaxMod | Module with the maximum temperature. | uint16 | string.1 | FALSE | TRUE
208 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMin | Minimum temperature for all modules in the bank. | int16 | string.1 | TRUE | TRUE
209 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMinMod | Module with the minimum temperature. | uint16 | string.1 | FALSE | TRUE
210 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpAvg | Average temperature for all modules in the bank. | int16 | string.1 | TRUE | TRUE
211 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrDisRsn | Reason why the string is currently disabled. | enum16 | string.1 | FALSE | FALSE
212 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrConSt | Status of the contactor(s) for the string. | bitfield32 | string.1 | FALSE | FALSE
214 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | Alarms, warnings and status values. Bit flags. | bitfield32 | string.1 | TRUE | TRUE
216 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt2 | Alarms, warnings and status values. Bit flags. | bitfield32 | string.1 | FALSE | FALSE
218 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvtVnd1 | Vendor defined events. | bitfield32 | string.1 | FALSE | FALSE
220 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvtVnd2 | Vendor defined events. | bitfield32 | string.1 | FALSE | FALSE
222 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetEna | Enables and disables the string. | enum16 | string.1 | FALSE | TRUE
223 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetCon | Connects and disconnects the string. | enum16 | string.1 | FALSE | TRUE
224 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.Pad1 | Pad register. | pad | string.1 | TRUE | TRUE
225 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.Pad2 | Pad register. | pad | string.1 | TRUE | TRUE
226 | lithium_ion_string | Lithium-Ion String Model | ID | Model identifier | uint16 |  | TRUE | TRUE
227 | lithium_ion_string | Lithium-Ion String Model | L | Model length | uint16 |  | TRUE | TRUE
228 | lithium_ion_string | Lithium-Ion String Model | Idx | Index of the string within the bank. | uint16 |  | TRUE | TRUE
229 | lithium_ion_string | Lithium-Ion String Model | NMod | Count of modules in the string. | uint16 |  | TRUE | TRUE
230 | lithium_ion_string | Lithium-Ion String Model | St | Current status of the string. | bitfield32 |  | TRUE | TRUE
232 | lithium_ion_string | Lithium-Ion String Model | ConFail |  | enum16 |  | FALSE | FALSE
233 | lithium_ion_string | Lithium-Ion String Model | NCellBal | Number of cells currently being balanced in the string. | uint16 |  | FALSE | FALSE
234 | lithium_ion_string | Lithium-Ion String Model | SoC | Battery string state of charge, expressed as a percentage. | uint16 |  | TRUE | TRUE
235 | lithium_ion_string | Lithium-Ion String Model | DoD | Depth of discharge for the string, expressed as a percentage. | uint16 |  | FALSE | FALSE
236 | lithium_ion_string | Lithium-Ion String Model | NCyc | Number of discharge cycles executed upon the string. | uint32 |  | FALSE | FALSE
238 | lithium_ion_string | Lithium-Ion String Model | SoH | Battery string state of health, expressed as a percentage. | uint16 |  | FALSE | TRUE
239 | lithium_ion_string | Lithium-Ion String Model | A | String current measurement. | int16 |  | TRUE | TRUE
240 | lithium_ion_string | Lithium-Ion String Model | V | String voltage measurement. | uint16 |  | FALSE | TRUE
241 | lithium_ion_string | Lithium-Ion String Model | CellVMax | Maximum voltage for all cells in the string. | uint16 |  | TRUE | TRUE
242 | lithium_ion_string | Lithium-Ion String Model | CellVMaxMod | Module containing the cell with maximum cell voltage. | uint16 |  | FALSE | FALSE
243 | lithium_ion_string | Lithium-Ion String Model | CellVMin | Minimum voltage for all cells in the string. | uint16 |  | TRUE | TRUE
244 | lithium_ion_string | Lithium-Ion String Model | CellVMinMod | Module containing the cell with minimum cell voltage. | uint16 |  | FALSE | FALSE
245 | lithium_ion_string | Lithium-Ion String Model | CellVAvg | Average voltage for all cells in the string. | uint16 |  | TRUE | TRUE
246 | lithium_ion_string | Lithium-Ion String Model | ModTmpMax | Maximum temperature for all modules in the string. | int16 |  | TRUE | TRUE
247 | lithium_ion_string | Lithium-Ion String Model | ModTmpMaxMod | Module with the maximum temperature. | uint16 |  | TRUE | TRUE
248 | lithium_ion_string | Lithium-Ion String Model | ModTmpMin | Minimum temperature for all modules in the string. | int16 |  | TRUE | TRUE
249 | lithium_ion_string | Lithium-Ion String Model | ModTmpMinMod | Module with the minimum temperature. | uint16 |  | TRUE | TRUE
250 | lithium_ion_string | Lithium-Ion String Model | ModTmpAvg | Average temperature for all modules in the string. | int16 |  | TRUE | TRUE
251 | lithium_ion_string | Lithium-Ion String Model | Pad1 | Pad register. | pad |  | TRUE | TRUE
252 | lithium_ion_string | Lithium-Ion String Model | ConSt | Status of the contactor(s) for the string. | bitfield32 |  | FALSE | FALSE
254 | lithium_ion_string | Lithium-Ion String Model | Evt1 | Alarms, warnings and status values. Bit flags. | bitfield32 |  | TRUE | TRUE
256 | lithium_ion_string | Lithium-Ion String Model | Evt2 | Alarms, warnings and status values. Bit flags. | bitfield32 |  | FALSE | FALSE
258 | lithium_ion_string | Lithium-Ion String Model | EvtVnd1 | Vendor defined events. | bitfield32 |  | FALSE | FALSE
260 | lithium_ion_string | Lithium-Ion String Model | EvtVnd2 | Vendor defined events. | bitfield32 |  | FALSE | FALSE
262 | lithium_ion_string | Lithium-Ion String Model | SetEna | Enables and disables the string. Should reset to 0 upon completion. | enum16 |  | FALSE | FALSE
263 | lithium_ion_string | Lithium-Ion String Model | SetCon | Connects and disconnects the string. | enum16 |  | FALSE | FALSE
264 | lithium_ion_string | Lithium-Ion String Model | SoC_SF | Scale factor for string state of charge. | sunssf |  | TRUE | TRUE
265 | lithium_ion_string | Lithium-Ion String Model | SoH_SF | Scale factor for string state of health. | sunssf |  | FALSE | TRUE
266 | lithium_ion_string | Lithium-Ion String Model | DoD_SF | Scale factor for string depth of discharge. | sunssf |  | FALSE | FALSE
267 | lithium_ion_string | Lithium-Ion String Model | A_SF | Scale factor for string current. | sunssf |  | TRUE | TRUE
268 | lithium_ion_string | Lithium-Ion String Model | V_SF | Scale factor for string voltage. | sunssf |  | FALSE | TRUE
269 | lithium_ion_string | Lithium-Ion String Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
270 | lithium_ion_string | Lithium-Ion String Model | ModTmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
271 | lithium_ion_string | Lithium-Ion String Model | Pad2 | Pad register. | pad |  | TRUE | TRUE
272 | lithium_ion_string | Lithium-Ion String Model | Pad3 | Pad register. | pad |  | TRUE | TRUE
273 | lithium_ion_string | Lithium-Ion String Model | Pad4 | Pad register. | pad |  | TRUE | TRUE
274 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
275 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.0 | FALSE | FALSE
276 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.0 | FALSE | FALSE
277 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
278 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
279 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
280 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
281 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
282 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
283 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
284 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
285 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
286 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
287 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
288 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
289 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
290 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
291 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.1 | FALSE | FALSE
292 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.1 | FALSE | FALSE
293 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
294 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
295 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
296 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
297 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
298 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
299 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
300 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
301 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
302 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
303 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
304 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
305 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
306 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
307 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.2 | FALSE | FALSE
308 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.2 | FALSE | FALSE
309 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
310 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
311 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
312 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
313 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
314 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
315 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
316 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
317 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
318 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
319 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
320 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
321 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
322 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
323 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.3 | FALSE | FALSE
324 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.3 | FALSE | FALSE
325 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
326 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
327 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
328 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
329 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
330 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
331 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
332 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
333 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
334 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
335 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
336 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
337 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
338 | lithium_ion_string | Lithium-Ion String Model | ID | Model identifier | uint16 |  | TRUE | TRUE
339 | lithium_ion_string | Lithium-Ion String Model | L | Model length | uint16 |  | TRUE | TRUE
340 | lithium_ion_string | Lithium-Ion String Model | Idx | Index of the string within the bank. | uint16 |  | TRUE | TRUE
341 | lithium_ion_string | Lithium-Ion String Model | NMod | Count of modules in the string. | uint16 |  | TRUE | TRUE
342 | lithium_ion_string | Lithium-Ion String Model | St | Current status of the string. | bitfield32 |  | TRUE | TRUE
344 | lithium_ion_string | Lithium-Ion String Model | ConFail |  | enum16 |  | FALSE | FALSE
345 | lithium_ion_string | Lithium-Ion String Model | NCellBal | Number of cells currently being balanced in the string. | uint16 |  | FALSE | FALSE
346 | lithium_ion_string | Lithium-Ion String Model | SoC | Battery string state of charge, expressed as a percentage. | uint16 |  | TRUE | TRUE
347 | lithium_ion_string | Lithium-Ion String Model | DoD | Depth of discharge for the string, expressed as a percentage. | uint16 |  | FALSE | FALSE
348 | lithium_ion_string | Lithium-Ion String Model | NCyc | Number of discharge cycles executed upon the string. | uint32 |  | FALSE | FALSE
350 | lithium_ion_string | Lithium-Ion String Model | SoH | Battery string state of health, expressed as a percentage. | uint16 |  | FALSE | TRUE
351 | lithium_ion_string | Lithium-Ion String Model | A | String current measurement. | int16 |  | TRUE | TRUE
352 | lithium_ion_string | Lithium-Ion String Model | V | String voltage measurement. | uint16 |  | FALSE | TRUE
353 | lithium_ion_string | Lithium-Ion String Model | CellVMax | Maximum voltage for all cells in the string. | uint16 |  | TRUE | TRUE
354 | lithium_ion_string | Lithium-Ion String Model | CellVMaxMod | Module containing the cell with maximum cell voltage. | uint16 |  | FALSE | FALSE
355 | lithium_ion_string | Lithium-Ion String Model | CellVMin | Minimum voltage for all cells in the string. | uint16 |  | TRUE | TRUE
356 | lithium_ion_string | Lithium-Ion String Model | CellVMinMod | Module containing the cell with minimum cell voltage. | uint16 |  | FALSE | FALSE
357 | lithium_ion_string | Lithium-Ion String Model | CellVAvg | Average voltage for all cells in the string. | uint16 |  | TRUE | TRUE
358 | lithium_ion_string | Lithium-Ion String Model | ModTmpMax | Maximum temperature for all modules in the string. | int16 |  | TRUE | TRUE
359 | lithium_ion_string | Lithium-Ion String Model | ModTmpMaxMod | Module with the maximum temperature. | uint16 |  | TRUE | TRUE
360 | lithium_ion_string | Lithium-Ion String Model | ModTmpMin | Minimum temperature for all modules in the string. | int16 |  | TRUE | TRUE
361 | lithium_ion_string | Lithium-Ion String Model | ModTmpMinMod | Module with the minimum temperature. | uint16 |  | TRUE | TRUE
362 | lithium_ion_string | Lithium-Ion String Model | ModTmpAvg | Average temperature for all modules in the string. | int16 |  | TRUE | TRUE
363 | lithium_ion_string | Lithium-Ion String Model | Pad1 | Pad register. | pad |  | TRUE | TRUE
364 | lithium_ion_string | Lithium-Ion String Model | ConSt | Status of the contactor(s) for the string. | bitfield32 |  | FALSE | FALSE
366 | lithium_ion_string | Lithium-Ion String Model | Evt1 | Alarms, warnings and status values. Bit flags. | bitfield32 |  | TRUE | TRUE
368 | lithium_ion_string | Lithium-Ion String Model | Evt2 | Alarms, warnings and status values. Bit flags. | bitfield32 |  | FALSE | FALSE
370 | lithium_ion_string | Lithium-Ion String Model | EvtVnd1 | Vendor defined events. | bitfield32 |  | FALSE | FALSE
372 | lithium_ion_string | Lithium-Ion String Model | EvtVnd2 | Vendor defined events. | bitfield32 |  | FALSE | FALSE
374 | lithium_ion_string | Lithium-Ion String Model | SetEna | Enables and disables the string. Should reset to 0 upon completion. | enum16 |  | FALSE | FALSE
375 | lithium_ion_string | Lithium-Ion String Model | SetCon | Connects and disconnects the string. | enum16 |  | FALSE | FALSE
376 | lithium_ion_string | Lithium-Ion String Model | SoC_SF | Scale factor for string state of charge. | sunssf |  | TRUE | TRUE
377 | lithium_ion_string | Lithium-Ion String Model | SoH_SF | Scale factor for string state of health. | sunssf |  | FALSE | TRUE
378 | lithium_ion_string | Lithium-Ion String Model | DoD_SF | Scale factor for string depth of discharge. | sunssf |  | FALSE | FALSE
379 | lithium_ion_string | Lithium-Ion String Model | A_SF | Scale factor for string current. | sunssf |  | TRUE | TRUE
380 | lithium_ion_string | Lithium-Ion String Model | V_SF | Scale factor for string voltage. | sunssf |  | FALSE | TRUE
381 | lithium_ion_string | Lithium-Ion String Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
382 | lithium_ion_string | Lithium-Ion String Model | ModTmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
383 | lithium_ion_string | Lithium-Ion String Model | Pad2 | Pad register. | pad |  | TRUE | TRUE
384 | lithium_ion_string | Lithium-Ion String Model | Pad3 | Pad register. | pad |  | TRUE | TRUE
385 | lithium_ion_string | Lithium-Ion String Model | Pad4 | Pad register. | pad |  | TRUE | TRUE
386 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
387 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.0 | FALSE | FALSE
388 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.0 | FALSE | FALSE
389 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
390 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
391 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
392 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
393 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
394 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
395 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
396 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
397 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
398 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
399 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
400 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
401 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
402 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
403 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.1 | FALSE | FALSE
404 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.1 | FALSE | FALSE
405 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
406 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
407 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
408 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
409 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
410 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
411 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
412 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
413 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
414 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
415 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
416 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
417 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
418 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
419 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.2 | FALSE | FALSE
420 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.2 | FALSE | FALSE
421 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
422 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
423 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
424 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
425 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
426 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
427 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
428 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
429 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
430 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
431 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
432 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
433 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
434 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
435 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.3 | FALSE | FALSE
436 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.3 | FALSE | FALSE
437 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
438 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
439 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
440 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
441 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
442 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
443 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
444 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
445 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
446 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
447 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
448 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
449 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
450 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
451 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
452 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
453 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
454 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
455 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
456 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
457 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
458 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
460 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
461 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
462 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
463 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
464 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
465 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
466 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
467 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
468 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
469 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
470 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
471 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
472 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
488 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
489 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
490 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
491 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
492 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
493 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
494 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
495 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
496 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
498 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
499 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
500 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
502 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
503 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
504 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
506 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
507 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
508 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
510 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
511 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
512 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
514 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
515 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
516 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
518 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
519 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
520 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
522 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
523 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
524 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
526 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
527 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
528 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
530 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
531 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
532 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
534 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
535 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
536 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
538 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
539 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
540 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
542 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
543 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
544 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
546 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
547 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
548 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
550 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
551 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
552 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
554 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
555 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
556 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
558 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.16 | TRUE | TRUE
559 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.16 | TRUE | TRUE
560 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.16 | FALSE | TRUE
562 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.17 | TRUE | TRUE
563 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.17 | TRUE | TRUE
564 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.17 | FALSE | TRUE
566 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.18 | TRUE | TRUE
567 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.18 | TRUE | TRUE
568 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.18 | FALSE | TRUE
570 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.19 | TRUE | TRUE
571 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.19 | TRUE | TRUE
572 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.19 | FALSE | TRUE
574 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.20 | TRUE | TRUE
575 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.20 | TRUE | TRUE
576 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.20 | FALSE | TRUE
578 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.21 | TRUE | TRUE
579 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.21 | TRUE | TRUE
580 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.21 | FALSE | TRUE
582 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.22 | TRUE | TRUE
583 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.22 | TRUE | TRUE
584 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.22 | FALSE | TRUE
586 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.23 | TRUE | TRUE
587 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.23 | TRUE | TRUE
588 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.23 | FALSE | TRUE
590 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
591 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
592 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
593 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
594 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
595 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
596 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
597 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
598 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
600 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
601 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
602 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
603 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
604 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
605 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
606 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
607 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
608 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
609 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
610 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
611 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
612 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
628 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
629 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
630 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
631 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
632 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
633 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
634 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
635 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
636 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
638 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
639 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
640 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
642 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
643 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
644 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
646 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
647 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
648 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
650 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
651 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
652 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
654 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
655 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
656 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
658 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
659 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
660 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
662 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
663 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
664 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
666 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
667 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
668 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
670 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
671 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
672 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
674 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
675 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
676 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
678 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
679 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
680 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
682 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
683 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
684 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
686 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
687 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
688 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
690 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
691 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
692 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
694 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
695 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
696 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
698 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.16 | TRUE | TRUE
699 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.16 | TRUE | TRUE
700 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.16 | FALSE | TRUE
702 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.17 | TRUE | TRUE
703 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.17 | TRUE | TRUE
704 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.17 | FALSE | TRUE
706 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.18 | TRUE | TRUE
707 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.18 | TRUE | TRUE
708 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.18 | FALSE | TRUE
710 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.19 | TRUE | TRUE
711 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.19 | TRUE | TRUE
712 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.19 | FALSE | TRUE
714 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.20 | TRUE | TRUE
715 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.20 | TRUE | TRUE
716 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.20 | FALSE | TRUE
718 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.21 | TRUE | TRUE
719 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.21 | TRUE | TRUE
720 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.21 | FALSE | TRUE
722 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.22 | TRUE | TRUE
723 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.22 | TRUE | TRUE
724 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.22 | FALSE | TRUE
726 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.23 | TRUE | TRUE
727 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.23 | TRUE | TRUE
728 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.23 | FALSE | TRUE
730 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
731 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
732 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
733 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
734 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
735 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
736 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
737 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
738 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
740 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
741 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
742 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
743 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
744 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
745 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
746 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
747 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
748 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
749 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
750 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
751 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
752 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
768 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
769 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
770 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
771 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
772 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
773 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
774 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
775 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
776 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
778 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
779 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
780 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
782 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
783 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
784 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
786 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
787 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
788 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
790 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
791 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
792 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
794 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
795 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
796 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
798 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
799 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
800 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
802 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
803 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
804 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
806 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
807 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
808 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
810 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
811 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
812 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
814 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
815 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
816 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
818 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
819 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
820 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
822 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
823 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
824 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
826 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
827 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
828 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
830 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
831 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
832 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
834 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
835 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
836 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
838 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.16 | TRUE | TRUE
839 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.16 | TRUE | TRUE
840 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.16 | FALSE | TRUE
842 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.17 | TRUE | TRUE
843 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.17 | TRUE | TRUE
844 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.17 | FALSE | TRUE
846 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.18 | TRUE | TRUE
847 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.18 | TRUE | TRUE
848 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.18 | FALSE | TRUE
850 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.19 | TRUE | TRUE
851 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.19 | TRUE | TRUE
852 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.19 | FALSE | TRUE
854 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.20 | TRUE | TRUE
855 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.20 | TRUE | TRUE
856 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.20 | FALSE | TRUE
858 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.21 | TRUE | TRUE
859 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.21 | TRUE | TRUE
860 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.21 | FALSE | TRUE
862 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.22 | TRUE | TRUE
863 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.22 | TRUE | TRUE
864 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.22 | FALSE | TRUE
866 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.23 | TRUE | TRUE
867 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.23 | TRUE | TRUE
868 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.23 | FALSE | TRUE
870 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
871 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
872 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
873 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
874 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
875 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
876 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
877 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
878 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
880 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
881 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
882 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
883 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
884 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
885 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
886 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
887 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
888 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
889 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
890 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
891 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
892 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
908 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
909 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
910 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
911 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
912 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
913 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
914 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
915 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
916 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
918 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
919 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
920 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
922 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
923 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
924 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
926 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
927 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
928 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
930 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
931 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
932 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
934 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
935 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
936 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
938 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
939 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
940 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
942 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
943 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
944 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
946 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
947 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
948 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
950 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
951 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
952 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
954 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
955 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
956 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
958 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
959 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
960 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
962 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
963 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
964 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
966 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
967 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
968 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
970 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
971 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
972 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
974 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
975 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
976 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
978 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.16 | TRUE | TRUE
979 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.16 | TRUE | TRUE
980 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.16 | FALSE | TRUE
982 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.17 | TRUE | TRUE
983 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.17 | TRUE | TRUE
984 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.17 | FALSE | TRUE
986 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.18 | TRUE | TRUE
987 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.18 | TRUE | TRUE
988 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.18 | FALSE | TRUE
990 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.19 | TRUE | TRUE
991 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.19 | TRUE | TRUE
992 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.19 | FALSE | TRUE
994 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.20 | TRUE | TRUE
995 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.20 | TRUE | TRUE
996 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.20 | FALSE | TRUE
998 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.21 | TRUE | TRUE
999 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.21 | TRUE | TRUE
1000 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.21 | FALSE | TRUE
1002 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.22 | TRUE | TRUE
1003 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.22 | TRUE | TRUE
1004 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.22 | FALSE | TRUE
1006 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.23 | TRUE | TRUE
1007 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.23 | TRUE | TRUE
1008 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.23 | FALSE | TRUE
1010 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
1011 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
1012 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
1013 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
1014 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
1015 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
1016 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
1017 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
1018 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
1020 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
1021 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1022 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
1023 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1024 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
1025 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1026 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1027 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
1028 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1029 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
1030 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
1031 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
1032 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
1048 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
1049 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
1050 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
1051 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
1052 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
1053 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
1054 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
1055 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
1056 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
1058 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
1059 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
1060 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
1062 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
1063 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
1064 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
1066 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
1067 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
1068 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
1070 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
1071 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
1072 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
1074 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
1075 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
1076 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
1078 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
1079 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
1080 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
1082 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
1083 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
1084 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
1086 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
1087 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
1088 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
1090 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
1091 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
1092 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
1094 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
1095 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
1096 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
1098 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
1099 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
1100 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
1102 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
1103 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
1104 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
1106 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
1107 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
1108 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
1110 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
1111 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
1112 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
1114 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
1115 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
1116 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
1118 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.16 | TRUE | TRUE
1119 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.16 | TRUE | TRUE
1120 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.16 | FALSE | TRUE
1122 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.17 | TRUE | TRUE
1123 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.17 | TRUE | TRUE
1124 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.17 | FALSE | TRUE
1126 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.18 | TRUE | TRUE
1127 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.18 | TRUE | TRUE
1128 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.18 | FALSE | TRUE
1130 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.19 | TRUE | TRUE
1131 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.19 | TRUE | TRUE
1132 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.19 | FALSE | TRUE
1134 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.20 | TRUE | TRUE
1135 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.20 | TRUE | TRUE
1136 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.20 | FALSE | TRUE
1138 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.21 | TRUE | TRUE
1139 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.21 | TRUE | TRUE
1140 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.21 | FALSE | TRUE
1142 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.22 | TRUE | TRUE
1143 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.22 | TRUE | TRUE
1144 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.22 | FALSE | TRUE
1146 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.23 | TRUE | TRUE
1147 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.23 | TRUE | TRUE
1148 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.23 | FALSE | TRUE
1150 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
1151 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
1152 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
1153 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
1154 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
1155 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
1156 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
1157 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
1158 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
1160 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
1161 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1162 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
1163 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1164 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
1165 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1166 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1167 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
1168 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1169 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
1170 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
1171 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
1172 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
1188 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
1189 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
1190 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
1191 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
1192 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
1193 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
1194 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
1195 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
1196 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
1198 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
1199 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
1200 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
1202 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
1203 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
1204 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
1206 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
1207 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
1208 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
1210 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
1211 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
1212 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
1214 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
1215 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
1216 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
1218 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
1219 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
1220 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
1222 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
1223 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
1224 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
1226 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
1227 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
1228 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
1230 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
1231 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
1232 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
1234 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
1235 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
1236 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
1238 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
1239 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
1240 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
1242 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
1243 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
1244 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
1246 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
1247 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
1248 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
1250 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
1251 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
1252 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
1254 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
1255 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
1256 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
1258 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.16 | TRUE | TRUE
1259 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.16 | TRUE | TRUE
1260 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.16 | FALSE | TRUE
1262 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.17 | TRUE | TRUE
1263 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.17 | TRUE | TRUE
1264 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.17 | FALSE | TRUE
1266 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.18 | TRUE | TRUE
1267 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.18 | TRUE | TRUE
1268 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.18 | FALSE | TRUE
1270 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.19 | TRUE | TRUE
1271 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.19 | TRUE | TRUE
1272 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.19 | FALSE | TRUE
1274 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.20 | TRUE | TRUE
1275 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.20 | TRUE | TRUE
1276 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.20 | FALSE | TRUE
1278 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.21 | TRUE | TRUE
1279 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.21 | TRUE | TRUE
1280 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.21 | FALSE | TRUE
1282 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.22 | TRUE | TRUE
1283 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.22 | TRUE | TRUE
1284 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.22 | FALSE | TRUE
1286 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.23 | TRUE | TRUE
1287 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.23 | TRUE | TRUE
1288 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.23 | FALSE | TRUE
1290 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
1291 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
1292 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
1293 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
1294 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
1295 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
1296 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
1297 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
1298 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
1300 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
1301 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1302 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
1303 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1304 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
1305 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1306 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1307 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
1308 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1309 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
1310 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
1311 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
1312 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
1328 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
1329 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
1330 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
1331 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
1332 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
1333 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
1334 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
1335 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
1336 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
1338 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
1339 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
1340 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
1342 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
1343 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
1344 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
1346 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
1347 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
1348 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
1350 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
1351 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
1352 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
1354 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
1355 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
1356 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
1358 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
1359 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
1360 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
1362 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
1363 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
1364 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
1366 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
1367 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
1368 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
1370 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
1371 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
1372 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
1374 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
1375 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
1376 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
1378 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
1379 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
1380 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
1382 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
1383 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
1384 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
1386 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
1387 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
1388 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
1390 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
1391 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
1392 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
1394 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
1395 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
1396 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
1398 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.16 | TRUE | TRUE
1399 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.16 | TRUE | TRUE
1400 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.16 | FALSE | TRUE
1402 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.17 | TRUE | TRUE
1403 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.17 | TRUE | TRUE
1404 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.17 | FALSE | TRUE
1406 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.18 | TRUE | TRUE
1407 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.18 | TRUE | TRUE
1408 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.18 | FALSE | TRUE
1410 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.19 | TRUE | TRUE
1411 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.19 | TRUE | TRUE
1412 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.19 | FALSE | TRUE
1414 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.20 | TRUE | TRUE
1415 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.20 | TRUE | TRUE
1416 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.20 | FALSE | TRUE
1418 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.21 | TRUE | TRUE
1419 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.21 | TRUE | TRUE
1420 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.21 | FALSE | TRUE
1422 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.22 | TRUE | TRUE
1423 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.22 | TRUE | TRUE
1424 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.22 | FALSE | TRUE
1426 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.23 | TRUE | TRUE
1427 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.23 | TRUE | TRUE
1428 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.23 | FALSE | TRUE
1430 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
1431 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
1432 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
1433 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
1434 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
1435 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
1436 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
1437 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
1438 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
1440 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
1441 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1442 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
1443 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1444 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
1445 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1446 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1447 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
1448 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1449 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
1450 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
1451 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
1452 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
1468 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
1469 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
1470 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
1471 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
1472 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
1473 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
1474 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
1475 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
1476 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
1478 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
1479 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
1480 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
1482 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
1483 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
1484 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
1486 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
1487 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
1488 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
1490 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
1491 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
1492 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
1494 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
1495 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
1496 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
1498 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
1499 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
1500 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
1502 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
1503 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
1504 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
1506 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
1507 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
1508 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
1510 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
1511 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
1512 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
1514 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
1515 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
1516 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
1518 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
1519 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
1520 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
1522 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
1523 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
1524 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
1526 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
1527 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
1528 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
1530 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
1531 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
1532 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
1534 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
1535 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
1536 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
1538 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.16 | TRUE | TRUE
1539 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.16 | TRUE | TRUE
1540 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.16 | FALSE | TRUE
1542 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.17 | TRUE | TRUE
1543 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.17 | TRUE | TRUE
1544 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.17 | FALSE | TRUE
1546 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.18 | TRUE | TRUE
1547 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.18 | TRUE | TRUE
1548 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.18 | FALSE | TRUE
1550 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.19 | TRUE | TRUE
1551 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.19 | TRUE | TRUE
1552 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.19 | FALSE | TRUE
1554 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.20 | TRUE | TRUE
1555 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.20 | TRUE | TRUE
1556 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.20 | FALSE | TRUE
1558 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.21 | TRUE | TRUE
1559 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.21 | TRUE | TRUE
1560 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.21 | FALSE | TRUE
1562 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.22 | TRUE | TRUE
1563 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.22 | TRUE | TRUE
1564 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.22 | FALSE | TRUE
1566 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.23 | TRUE | TRUE
1567 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.23 | TRUE | TRUE
1568 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.23 | FALSE | TRUE
1570 | end | End | ID | Model identifier | uint16 |  | TRUE | TRUE
1571 | end | End | L | Model length | uint16 |  | TRUE | TRUE

## Sample_Map_4Stack_18CI_16Cell
Offset | Model | Model Label | Name | Description | Type | Group | Mandatory | Implemented
0 | Start | start | mmid_hi | Model map identifier hi | uint16 |  | TRUE | TRUE
1 | Start | start | mmid_lo | Model map identifier lo | uint16 |  | TRUE | TRUE
2 | common | Common | ID | Model identifier | uint16 |  | TRUE | TRUE
3 | common | Common | L | Model length | uint16 |  | TRUE | TRUE
4 | common | Common | Mn | Well known value registered with SunSpec for compliance | string |  | TRUE | TRUE
20 | common | Common | Md | Manufacturer specific value (32 chars) | string |  | TRUE | TRUE
36 | common | Common | Opt | Manufacturer specific value (16 chars) | string |  | FALSE | TRUE
44 | common | Common | Vr | Manufacturer specific value (16 chars) | string |  | FALSE | TRUE
52 | common | Common | SN | Manufacturer specific value (32 chars) | string |  | TRUE | TRUE
68 | common | Common | DA | Modbus device address | uint16 |  | FALSE | TRUE
69 | common | Common | Pad | Force even alignment | pad |  | FALSE | TRUE
70 | battery | Battery Base Model | ID | Model identifier | uint16 |  | TRUE | TRUE
71 | battery | Battery Base Model | L | Model length | uint16 |  | TRUE | TRUE
72 | battery | Battery Base Model | AHRtg | Nameplate charge capacity in amp-hours. | uint16 |  | TRUE | TRUE
73 | battery | Battery Base Model | WHRtg | Nameplate energy capacity in DC watt-hours. | uint16 |  | TRUE | TRUE
74 | battery | Battery Base Model | WChaRteMax | Maximum rate of energy transfer into the storage device in DC watts. | uint16 |  | TRUE | TRUE
75 | battery | Battery Base Model | WDisChaRteMax | Maximum rate of energy transfer out of the storage device in DC watts. | uint16 |  | TRUE | TRUE
76 | battery | Battery Base Model | DisChaRte | Self discharge rate. Percentage of capacity (WHRtg) discharged per day. | uint16 |  | FALSE | FALSE
77 | battery | Battery Base Model | SoCMax | Manufacturer maximum state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
78 | battery | Battery Base Model | SoCMin | Manufacturer minimum state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
79 | battery | Battery Base Model | SocRsvMax | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage. | uint16 |  | FALSE | FALSE
80 | battery | Battery Base Model | SoCRsvMin | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage. | uint16 |  | FALSE | FALSE
81 | battery | Battery Base Model | SoC | State of charge, expressed as a percentage. | uint16 |  | TRUE | TRUE
82 | battery | Battery Base Model | DoD | Depth of discharge, expressed as a percentage. | uint16 |  | FALSE | FALSE
83 | battery | Battery Base Model | SoH | Percentage of battery life remaining. | uint16 |  | FALSE | TRUE
84 | battery | Battery Base Model | NCyc | Number of cycles executed in the battery. | uint32 |  | FALSE | FALSE
86 | battery | Battery Base Model | ChaSt | Charge status of storage device. Enumeration. | enum16 |  | FALSE | FALSE
87 | battery | Battery Base Model | LocRemCtl | Battery control mode. Enumeration. | enum16 |  | TRUE | TRUE
88 | battery | Battery Base Model | Hb | Value is incremented every second with periodic resets to zero. | uint16 |  | FALSE | TRUE
89 | battery | Battery Base Model | CtrlHb | Value is incremented every second with periodic resets to zero. | uint16 |  | FALSE | TRUE
90 | battery | Battery Base Model | AlmRst | Used to reset any latched alarms. 1 = Reset. | uint16 |  | TRUE | TRUE
91 | battery | Battery Base Model | Typ | Type of battery. Enumeration. | enum16 |  | TRUE | TRUE
92 | battery | Battery Base Model | State | State of the battery bank. Enumeration. | enum16 |  | TRUE | TRUE
93 | battery | Battery Base Model | StateVnd | Vendor specific battery bank state. Enumeration. | enum16 |  | FALSE | FALSE
94 | battery | Battery Base Model | WarrDt | Date the device warranty expires. | uint32 |  | FALSE | FALSE
96 | battery | Battery Base Model | Evt1 | Alarms and warnings. Bit flags. | bitfield32 |  | TRUE | TRUE
98 | battery | Battery Base Model | Evt2 | Alarms and warnings. Bit flags. | bitfield32 |  | TRUE | TRUE
100 | battery | Battery Base Model | EvtVnd1 | Vendor defined events. | bitfield32 |  | TRUE | TRUE
102 | battery | Battery Base Model | EvtVnd2 | Vendor defined events. | bitfield32 |  | TRUE | TRUE
104 | battery | Battery Base Model | V | DC Bus Voltage. | uint16 |  | TRUE | TRUE
105 | battery | Battery Base Model | VMax | Instantaneous maximum battery voltage. | uint16 |  | FALSE | FALSE
106 | battery | Battery Base Model | VMin | Instantaneous minimum battery voltage. | uint16 |  | FALSE | FALSE
107 | battery | Battery Base Model | CellVMax | Maximum voltage for all cells in the bank. | uint16 |  | FALSE | TRUE
108 | battery | Battery Base Model | CellVMaxStr | String containing the cell with maximum voltage. | uint16 |  | FALSE | TRUE
109 | battery | Battery Base Model | CellVMaxMod | Module containing the cell with maximum voltage. | uint16 |  | FALSE | FALSE
110 | battery | Battery Base Model | CellVMin | Minimum voltage for all cells in the bank. | uint16 |  | FALSE | TRUE
111 | battery | Battery Base Model | CellVMinStr | String containing the cell with minimum voltage. | uint16 |  | FALSE | TRUE
112 | battery | Battery Base Model | CellVMinMod | Module containing the cell with minimum voltage. | uint16 |  | FALSE | TRUE
113 | battery | Battery Base Model | CellVAvg | Average cell voltage for all cells in the bank. | uint16 |  | FALSE | TRUE
114 | battery | Battery Base Model | A | Total DC current flowing to/from the battery bank. | int16 |  | TRUE | TRUE
115 | battery | Battery Base Model | AChaMax | Instantaneous maximum DC charge current. | uint16 |  | FALSE | TRUE
116 | battery | Battery Base Model | ADisChaMax | Instantaneous maximum DC discharge current. | uint16 |  | FALSE | TRUE
117 | battery | Battery Base Model | W | Total power flowing to/from the battery bank. | int16 |  | TRUE | TRUE
118 | battery | Battery Base Model | ReqInvState | Request from battery to start or stop the inverter. Enumeration. | enum16 |  | FALSE | FALSE
119 | battery | Battery Base Model | ReqW | AC Power requested by battery. | int16 |  | FALSE | FALSE
120 | battery | Battery Base Model | SetOp | Instruct the battery bank to perform an operation such as connecting. Enumeration. | enum16 |  | TRUE | TRUE
121 | battery | Battery Base Model | SetInvState | Set the current state of the inverter. | enum16 |  | TRUE | TRUE
122 | battery | Battery Base Model | AHRtg_SF | Scale factor for charge capacity. | sunssf |  | TRUE | TRUE
123 | battery | Battery Base Model | WHRtg_SF | Scale factor for energy capacity. | sunssf |  | TRUE | TRUE
124 | battery | Battery Base Model | WChaDisChaMax_SF | Scale factor for maximum charge and discharge rate. | sunssf |  | TRUE | TRUE
125 | battery | Battery Base Model | DisChaRte_SF | Scale factor for self discharge rate. | sunssf |  | FALSE | FALSE
126 | battery | Battery Base Model | SoC_SF | Scale factor for state of charge values. | sunssf |  | TRUE | TRUE
127 | battery | Battery Base Model | DoD_SF | Scale factor for depth of discharge. | sunssf |  | FALSE | FALSE
128 | battery | Battery Base Model | SoH_SF | Scale factor for state of health. | sunssf |  | FALSE | TRUE
129 | battery | Battery Base Model | V_SF | Scale factor for DC bus voltage. | sunssf |  | TRUE | TRUE
130 | battery | Battery Base Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
131 | battery | Battery Base Model | A_SF | Scale factor for DC current. | sunssf |  | TRUE | TRUE
132 | battery | Battery Base Model | AMax_SF | Scale factor for instantaneous DC charge/discharge current. | sunssf |  | TRUE | TRUE
133 | battery | Battery Base Model | W_SF | Scale factor for AC power request. | sunssf |  | FALSE | TRUE
134 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ID | Model identifier | uint16 |  | TRUE | TRUE
135 | lithium_ion_bank | Lithium-Ion Battery Bank Model | L | Model length | uint16 |  | TRUE | TRUE
136 | lithium_ion_bank | Lithium-Ion Battery Bank Model | NStr | Number of strings in the bank. | uint16 |  | TRUE | TRUE
137 | lithium_ion_bank | Lithium-Ion Battery Bank Model | NStrCon | Number of strings with contactor closed. | uint16 |  | TRUE | TRUE
138 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpMax | Maximum temperature for all modules in the bank. | int16 |  | TRUE | TRUE
139 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpMaxStr | String containing the module with maximum temperature. | uint16 |  | FALSE | TRUE
140 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpMaxMod | Module with maximum temperature. | uint16 |  | FALSE | TRUE
141 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpMin | Minimum temperature for all modules in the bank. | int16 |  | TRUE | TRUE
142 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpMinStr | String containing the module with minimum temperature. | uint16 |  | FALSE | TRUE
143 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpMinMod | Module with minimum temperature. | uint16 |  | FALSE | TRUE
144 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmpAvg | Average temperature for all modules in the bank. | int16 |  | FALSE | TRUE
145 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrVMax | Maximum string voltage for all strings in the bank. | uint16 |  | FALSE | TRUE
146 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrVMaxStr | String with maximum voltage. | uint16 |  | FALSE | FALSE
147 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrVMin | Minimum string voltage for all strings in the bank. | uint16 |  | FALSE | TRUE
148 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrVMinStr | String with minimum voltage. | uint16 |  | FALSE | FALSE
149 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrVAvg | Average string voltage for all strings in the bank. | uint16 |  | FALSE | TRUE
150 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrAMax | Maximum current of any string in the bank. | int16 |  | FALSE | TRUE
151 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrAMaxStr | String with the maximum current. | uint16 |  | FALSE | FALSE
152 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrAMin | Minimum current of any string in the bank. | int16 |  | FALSE | TRUE
153 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrAMinStr | String with the minimum current. | uint16 |  | FALSE | FALSE
154 | lithium_ion_bank | Lithium-Ion Battery Bank Model | StrAAvg | Average string current for all strings in the bank. | int16 |  | FALSE | TRUE
155 | lithium_ion_bank | Lithium-Ion Battery Bank Model | NCellBal | Total number of cells that are currently being balanced. | uint16 |  | FALSE | FALSE
156 | lithium_ion_bank | Lithium-Ion Battery Bank Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
157 | lithium_ion_bank | Lithium-Ion Battery Bank Model | ModTmp_SF | Scale factor for module temperatures. | sunssf |  | TRUE | TRUE
158 | lithium_ion_bank | Lithium-Ion Battery Bank Model | A_SF | Scale factor for string currents. | sunssf |  | TRUE | TRUE
159 | lithium_ion_bank | Lithium-Ion Battery Bank Model | SoH_SF | Scale factor for string state of health. | sunssf |  | FALSE | TRUE
160 | lithium_ion_bank | Lithium-Ion Battery Bank Model | SoC_SF | Scale factor for string state of charge. | sunssf |  | TRUE | TRUE
161 | lithium_ion_bank | Lithium-Ion Battery Bank Model | V_SF | Scale factor for string voltage. | sunssf |  | FALSE | TRUE
162 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrNMod | Count of modules in the string. | uint16 | string.0 | TRUE | TRUE
163 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSt | Current status of the string. | bitfield32 | string.0 | TRUE | TRUE
165 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrConFail |  | enum16 | string.0 | FALSE | FALSE
166 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSoC | Battery string state of charge, expressed as a percentage. | uint16 | string.0 | TRUE | TRUE
167 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSoH | Battery string state of health, expressed as a percentage. | uint16 | string.0 | FALSE | TRUE
168 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrA | String current measurement. | int16 | string.0 | TRUE | TRUE
169 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMax | Maximum voltage for all cells in the string. | uint16 | string.0 | TRUE | TRUE
170 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMaxMod | Module containing the maximum cell voltage. | uint16 | string.0 | FALSE | TRUE
171 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMin | Minimum voltage for all cells in the string. | uint16 | string.0 | TRUE | TRUE
172 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMinMod | Module containing the minimum cell voltage. | uint16 | string.0 | FALSE | TRUE
173 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVAvg | Average voltage for all cells in the string. | uint16 | string.0 | TRUE | TRUE
174 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMax | Maximum temperature for all modules in the bank. | int16 | string.0 | TRUE | TRUE
175 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMaxMod | Module with the maximum temperature. | uint16 | string.0 | FALSE | TRUE
176 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMin | Minimum temperature for all modules in the bank. | int16 | string.0 | TRUE | TRUE
177 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMinMod | Module with the minimum temperature. | uint16 | string.0 | FALSE | TRUE
178 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpAvg | Average temperature for all modules in the bank. | int16 | string.0 | TRUE | TRUE
179 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrDisRsn | Reason why the string is currently disabled. | enum16 | string.0 | FALSE | FALSE
180 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrConSt | Status of the contactor(s) for the string. | bitfield32 | string.0 | FALSE | FALSE
182 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | Alarms, warnings and status values. Bit flags. | bitfield32 | string.0 | TRUE | TRUE
184 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt2 | Alarms, warnings and status values. Bit flags. | bitfield32 | string.0 | FALSE | FALSE
186 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvtVnd1 | Vendor defined events. | bitfield32 | string.0 | FALSE | FALSE
188 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvtVnd2 | Vendor defined events. | bitfield32 | string.0 | FALSE | FALSE
190 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetEna | Enables and disables the string. | enum16 | string.0 | FALSE | TRUE
191 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetCon | Connects and disconnects the string. | enum16 | string.0 | FALSE | TRUE
192 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.Pad1 | Pad register. | pad | string.0 | TRUE | TRUE
193 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.Pad2 | Pad register. | pad | string.0 | TRUE | TRUE
194 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrNMod | Count of modules in the string. | uint16 | string.1 | TRUE | TRUE
195 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSt | Current status of the string. | bitfield32 | string.1 | TRUE | TRUE
197 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrConFail |  | enum16 | string.1 | FALSE | FALSE
198 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSoC | Battery string state of charge, expressed as a percentage. | uint16 | string.1 | TRUE | TRUE
199 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSoH | Battery string state of health, expressed as a percentage. | uint16 | string.1 | FALSE | TRUE
200 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrA | String current measurement. | int16 | string.1 | TRUE | TRUE
201 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMax | Maximum voltage for all cells in the string. | uint16 | string.1 | TRUE | TRUE
202 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMaxMod | Module containing the maximum cell voltage. | uint16 | string.1 | FALSE | TRUE
203 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMin | Minimum voltage for all cells in the string. | uint16 | string.1 | TRUE | TRUE
204 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMinMod | Module containing the minimum cell voltage. | uint16 | string.1 | FALSE | TRUE
205 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVAvg | Average voltage for all cells in the string. | uint16 | string.1 | TRUE | TRUE
206 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMax | Maximum temperature for all modules in the bank. | int16 | string.1 | TRUE | TRUE
207 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMaxMod | Module with the maximum temperature. | uint16 | string.1 | FALSE | TRUE
208 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMin | Minimum temperature for all modules in the bank. | int16 | string.1 | TRUE | TRUE
209 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMinMod | Module with the minimum temperature. | uint16 | string.1 | FALSE | TRUE
210 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpAvg | Average temperature for all modules in the bank. | int16 | string.1 | TRUE | TRUE
211 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrDisRsn | Reason why the string is currently disabled. | enum16 | string.1 | FALSE | FALSE
212 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrConSt | Status of the contactor(s) for the string. | bitfield32 | string.1 | FALSE | FALSE
214 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | Alarms, warnings and status values. Bit flags. | bitfield32 | string.1 | TRUE | TRUE
216 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt2 | Alarms, warnings and status values. Bit flags. | bitfield32 | string.1 | FALSE | FALSE
218 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvtVnd1 | Vendor defined events. | bitfield32 | string.1 | FALSE | FALSE
220 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvtVnd2 | Vendor defined events. | bitfield32 | string.1 | FALSE | FALSE
222 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetEna | Enables and disables the string. | enum16 | string.1 | FALSE | TRUE
223 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetCon | Connects and disconnects the string. | enum16 | string.1 | FALSE | TRUE
224 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.Pad1 | Pad register. | pad | string.1 | TRUE | TRUE
225 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.Pad2 | Pad register. | pad | string.1 | TRUE | TRUE
226 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrNMod | Count of modules in the string. | uint16 | string.2 | TRUE | TRUE
227 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSt | Current status of the string. | bitfield32 | string.2 | TRUE | TRUE
229 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrConFail |  | enum16 | string.2 | FALSE | FALSE
230 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSoC | Battery string state of charge, expressed as a percentage. | uint16 | string.2 | TRUE | TRUE
231 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSoH | Battery string state of health, expressed as a percentage. | uint16 | string.2 | FALSE | TRUE
232 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrA | String current measurement. | int16 | string.2 | TRUE | TRUE
233 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMax | Maximum voltage for all cells in the string. | uint16 | string.2 | TRUE | TRUE
234 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMaxMod | Module containing the maximum cell voltage. | uint16 | string.2 | FALSE | TRUE
235 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMin | Minimum voltage for all cells in the string. | uint16 | string.2 | TRUE | TRUE
236 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMinMod | Module containing the minimum cell voltage. | uint16 | string.2 | FALSE | TRUE
237 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVAvg | Average voltage for all cells in the string. | uint16 | string.2 | TRUE | TRUE
238 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMax | Maximum temperature for all modules in the bank. | int16 | string.2 | TRUE | TRUE
239 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMaxMod | Module with the maximum temperature. | uint16 | string.2 | FALSE | TRUE
240 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMin | Minimum temperature for all modules in the bank. | int16 | string.2 | TRUE | TRUE
241 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMinMod | Module with the minimum temperature. | uint16 | string.2 | FALSE | TRUE
242 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpAvg | Average temperature for all modules in the bank. | int16 | string.2 | TRUE | TRUE
243 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrDisRsn | Reason why the string is currently disabled. | enum16 | string.2 | FALSE | FALSE
244 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrConSt | Status of the contactor(s) for the string. | bitfield32 | string.2 | FALSE | FALSE
246 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | Alarms, warnings and status values. Bit flags. | bitfield32 | string.2 | TRUE | TRUE
248 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt2 | Alarms, warnings and status values. Bit flags. | bitfield32 | string.2 | FALSE | FALSE
250 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvtVnd1 | Vendor defined events. | bitfield32 | string.2 | FALSE | FALSE
252 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvtVnd2 | Vendor defined events. | bitfield32 | string.2 | FALSE | FALSE
254 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetEna | Enables and disables the string. | enum16 | string.2 | FALSE | TRUE
255 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetCon | Connects and disconnects the string. | enum16 | string.2 | FALSE | TRUE
256 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.Pad1 | Pad register. | pad | string.2 | TRUE | TRUE
257 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.Pad2 | Pad register. | pad | string.2 | TRUE | TRUE
258 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrNMod | Count of modules in the string. | uint16 | string.3 | TRUE | TRUE
259 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSt | Current status of the string. | bitfield32 | string.3 | TRUE | TRUE
261 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrConFail |  | enum16 | string.3 | FALSE | FALSE
262 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSoC | Battery string state of charge, expressed as a percentage. | uint16 | string.3 | TRUE | TRUE
263 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSoH | Battery string state of health, expressed as a percentage. | uint16 | string.3 | FALSE | TRUE
264 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrA | String current measurement. | int16 | string.3 | TRUE | TRUE
265 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMax | Maximum voltage for all cells in the string. | uint16 | string.3 | TRUE | TRUE
266 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMaxMod | Module containing the maximum cell voltage. | uint16 | string.3 | FALSE | TRUE
267 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMin | Minimum voltage for all cells in the string. | uint16 | string.3 | TRUE | TRUE
268 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVMinMod | Module containing the minimum cell voltage. | uint16 | string.3 | FALSE | TRUE
269 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrCellVAvg | Average voltage for all cells in the string. | uint16 | string.3 | TRUE | TRUE
270 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMax | Maximum temperature for all modules in the bank. | int16 | string.3 | TRUE | TRUE
271 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMaxMod | Module with the maximum temperature. | uint16 | string.3 | FALSE | TRUE
272 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMin | Minimum temperature for all modules in the bank. | int16 | string.3 | TRUE | TRUE
273 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpMinMod | Module with the minimum temperature. | uint16 | string.3 | FALSE | TRUE
274 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrModTmpAvg | Average temperature for all modules in the bank. | int16 | string.3 | TRUE | TRUE
275 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrDisRsn | Reason why the string is currently disabled. | enum16 | string.3 | FALSE | FALSE
276 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrConSt | Status of the contactor(s) for the string. | bitfield32 | string.3 | FALSE | FALSE
278 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | Alarms, warnings and status values. Bit flags. | bitfield32 | string.3 | TRUE | TRUE
280 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt2 | Alarms, warnings and status values. Bit flags. | bitfield32 | string.3 | FALSE | FALSE
282 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvtVnd1 | Vendor defined events. | bitfield32 | string.3 | FALSE | FALSE
284 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvtVnd2 | Vendor defined events. | bitfield32 | string.3 | FALSE | FALSE
286 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetEna | Enables and disables the string. | enum16 | string.3 | FALSE | TRUE
287 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetCon | Connects and disconnects the string. | enum16 | string.3 | FALSE | TRUE
288 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.Pad1 | Pad register. | pad | string.3 | TRUE | TRUE
289 | lithium_ion_bank | Lithium-Ion Battery Bank Model | string.Pad2 | Pad register. | pad | string.3 | TRUE | TRUE
290 | lithium_ion_string | Lithium-Ion String Model | ID | Model identifier | uint16 |  | TRUE | TRUE
291 | lithium_ion_string | Lithium-Ion String Model | L | Model length | uint16 |  | TRUE | TRUE
292 | lithium_ion_string | Lithium-Ion String Model | Idx | Index of the string within the bank. | uint16 |  | TRUE | TRUE
293 | lithium_ion_string | Lithium-Ion String Model | NMod | Count of modules in the string. | uint16 |  | TRUE | TRUE
294 | lithium_ion_string | Lithium-Ion String Model | St | Current status of the string. | bitfield32 |  | TRUE | TRUE
296 | lithium_ion_string | Lithium-Ion String Model | ConFail |  | enum16 |  | FALSE | FALSE
297 | lithium_ion_string | Lithium-Ion String Model | NCellBal | Number of cells currently being balanced in the string. | uint16 |  | FALSE | FALSE
298 | lithium_ion_string | Lithium-Ion String Model | SoC | Battery string state of charge, expressed as a percentage. | uint16 |  | TRUE | TRUE
299 | lithium_ion_string | Lithium-Ion String Model | DoD | Depth of discharge for the string, expressed as a percentage. | uint16 |  | FALSE | FALSE
300 | lithium_ion_string | Lithium-Ion String Model | NCyc | Number of discharge cycles executed upon the string. | uint32 |  | FALSE | FALSE
302 | lithium_ion_string | Lithium-Ion String Model | SoH | Battery string state of health, expressed as a percentage. | uint16 |  | FALSE | TRUE
303 | lithium_ion_string | Lithium-Ion String Model | A | String current measurement. | int16 |  | TRUE | TRUE
304 | lithium_ion_string | Lithium-Ion String Model | V | String voltage measurement. | uint16 |  | FALSE | TRUE
305 | lithium_ion_string | Lithium-Ion String Model | CellVMax | Maximum voltage for all cells in the string. | uint16 |  | TRUE | TRUE
306 | lithium_ion_string | Lithium-Ion String Model | CellVMaxMod | Module containing the cell with maximum cell voltage. | uint16 |  | FALSE | FALSE
307 | lithium_ion_string | Lithium-Ion String Model | CellVMin | Minimum voltage for all cells in the string. | uint16 |  | TRUE | TRUE
308 | lithium_ion_string | Lithium-Ion String Model | CellVMinMod | Module containing the cell with minimum cell voltage. | uint16 |  | FALSE | FALSE
309 | lithium_ion_string | Lithium-Ion String Model | CellVAvg | Average voltage for all cells in the string. | uint16 |  | TRUE | TRUE
310 | lithium_ion_string | Lithium-Ion String Model | ModTmpMax | Maximum temperature for all modules in the string. | int16 |  | TRUE | TRUE
311 | lithium_ion_string | Lithium-Ion String Model | ModTmpMaxMod | Module with the maximum temperature. | uint16 |  | TRUE | TRUE
312 | lithium_ion_string | Lithium-Ion String Model | ModTmpMin | Minimum temperature for all modules in the string. | int16 |  | TRUE | TRUE
313 | lithium_ion_string | Lithium-Ion String Model | ModTmpMinMod | Module with the minimum temperature. | uint16 |  | TRUE | TRUE
314 | lithium_ion_string | Lithium-Ion String Model | ModTmpAvg | Average temperature for all modules in the string. | int16 |  | TRUE | TRUE
315 | lithium_ion_string | Lithium-Ion String Model | Pad1 | Pad register. | pad |  | TRUE | TRUE
316 | lithium_ion_string | Lithium-Ion String Model | ConSt | Status of the contactor(s) for the string. | bitfield32 |  | FALSE | FALSE
318 | lithium_ion_string | Lithium-Ion String Model | Evt1 | Alarms, warnings and status values. Bit flags. | bitfield32 |  | TRUE | TRUE
320 | lithium_ion_string | Lithium-Ion String Model | Evt2 | Alarms, warnings and status values. Bit flags. | bitfield32 |  | FALSE | FALSE
322 | lithium_ion_string | Lithium-Ion String Model | EvtVnd1 | Vendor defined events. | bitfield32 |  | FALSE | FALSE
324 | lithium_ion_string | Lithium-Ion String Model | EvtVnd2 | Vendor defined events. | bitfield32 |  | FALSE | FALSE
326 | lithium_ion_string | Lithium-Ion String Model | SetEna | Enables and disables the string. Should reset to 0 upon completion. | enum16 |  | FALSE | FALSE
327 | lithium_ion_string | Lithium-Ion String Model | SetCon | Connects and disconnects the string. | enum16 |  | FALSE | FALSE
328 | lithium_ion_string | Lithium-Ion String Model | SoC_SF | Scale factor for string state of charge. | sunssf |  | TRUE | TRUE
329 | lithium_ion_string | Lithium-Ion String Model | SoH_SF | Scale factor for string state of health. | sunssf |  | FALSE | TRUE
330 | lithium_ion_string | Lithium-Ion String Model | DoD_SF | Scale factor for string depth of discharge. | sunssf |  | FALSE | FALSE
331 | lithium_ion_string | Lithium-Ion String Model | A_SF | Scale factor for string current. | sunssf |  | TRUE | TRUE
332 | lithium_ion_string | Lithium-Ion String Model | V_SF | Scale factor for string voltage. | sunssf |  | FALSE | TRUE
333 | lithium_ion_string | Lithium-Ion String Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
334 | lithium_ion_string | Lithium-Ion String Model | ModTmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
335 | lithium_ion_string | Lithium-Ion String Model | Pad2 | Pad register. | pad |  | TRUE | TRUE
336 | lithium_ion_string | Lithium-Ion String Model | Pad3 | Pad register. | pad |  | TRUE | TRUE
337 | lithium_ion_string | Lithium-Ion String Model | Pad4 | Pad register. | pad |  | TRUE | TRUE
338 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
339 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.0 | FALSE | FALSE
340 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.0 | FALSE | FALSE
341 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
342 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
343 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
344 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
345 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
346 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
347 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
348 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
349 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
350 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
351 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
352 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
353 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
354 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
355 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.1 | FALSE | FALSE
356 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.1 | FALSE | FALSE
357 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
358 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
359 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
360 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
361 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
362 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
363 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
364 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
365 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
366 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
367 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
368 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
369 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
370 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
371 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.2 | FALSE | FALSE
372 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.2 | FALSE | FALSE
373 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
374 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
375 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
376 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
377 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
378 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
379 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
380 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
381 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
382 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
383 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
384 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
385 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
386 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
387 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.3 | FALSE | FALSE
388 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.3 | FALSE | FALSE
389 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
390 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
391 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
392 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
393 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
394 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
395 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
396 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
397 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
398 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
399 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
400 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
401 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
402 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
403 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.4 | FALSE | FALSE
404 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.4 | FALSE | FALSE
405 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
406 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
407 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
408 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
409 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
410 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.4 | TRUE | TRUE
411 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
412 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.4 | TRUE | TRUE
413 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
414 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.4 | TRUE | TRUE
415 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.4 | TRUE | TRUE
416 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.4 | TRUE | TRUE
417 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.4 | TRUE | TRUE
418 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
419 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.5 | FALSE | FALSE
420 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.5 | FALSE | FALSE
421 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
422 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
423 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
424 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
425 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
426 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.5 | TRUE | TRUE
427 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
428 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.5 | TRUE | TRUE
429 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
430 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.5 | TRUE | TRUE
431 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.5 | TRUE | TRUE
432 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.5 | TRUE | TRUE
433 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.5 | TRUE | TRUE
434 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
435 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.6 | FALSE | FALSE
436 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.6 | FALSE | FALSE
437 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
438 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
439 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
440 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
441 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
442 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.6 | TRUE | TRUE
443 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
444 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.6 | TRUE | TRUE
445 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
446 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.6 | TRUE | TRUE
447 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.6 | TRUE | TRUE
448 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.6 | TRUE | TRUE
449 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.6 | TRUE | TRUE
450 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
451 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.7 | FALSE | FALSE
452 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.7 | FALSE | FALSE
453 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
454 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
455 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
456 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
457 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
458 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.7 | TRUE | TRUE
459 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
460 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.7 | TRUE | TRUE
461 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
462 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.7 | TRUE | TRUE
463 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.7 | TRUE | TRUE
464 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.7 | TRUE | TRUE
465 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.7 | TRUE | TRUE
466 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
467 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.8 | FALSE | FALSE
468 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.8 | FALSE | FALSE
469 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
470 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
471 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
472 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
473 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
474 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.8 | TRUE | TRUE
475 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
476 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.8 | TRUE | TRUE
477 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
478 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.8 | TRUE | TRUE
479 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.8 | TRUE | TRUE
480 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.8 | TRUE | TRUE
481 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.8 | TRUE | TRUE
482 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
483 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.9 | FALSE | FALSE
484 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.9 | FALSE | FALSE
485 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
486 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
487 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
488 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
489 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
490 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.9 | TRUE | TRUE
491 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
492 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.9 | TRUE | TRUE
493 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
494 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.9 | TRUE | TRUE
495 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.9 | TRUE | TRUE
496 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.9 | TRUE | TRUE
497 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.9 | TRUE | TRUE
498 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
499 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.10 | FALSE | FALSE
500 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.10 | FALSE | FALSE
501 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
502 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
503 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
504 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
505 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
506 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.10 | TRUE | TRUE
507 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
508 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.10 | TRUE | TRUE
509 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
510 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.10 | TRUE | TRUE
511 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.10 | TRUE | TRUE
512 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.10 | TRUE | TRUE
513 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.10 | TRUE | TRUE
514 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
515 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.11 | FALSE | FALSE
516 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.11 | FALSE | FALSE
517 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
518 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
519 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
520 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
521 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
522 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.11 | TRUE | TRUE
523 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
524 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.11 | TRUE | TRUE
525 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
526 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.11 | TRUE | TRUE
527 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.11 | TRUE | TRUE
528 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.11 | TRUE | TRUE
529 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.11 | TRUE | TRUE
530 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
531 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.12 | FALSE | FALSE
532 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.12 | FALSE | FALSE
533 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
534 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
535 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
536 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
537 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
538 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.12 | TRUE | TRUE
539 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
540 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.12 | TRUE | TRUE
541 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
542 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.12 | TRUE | TRUE
543 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.12 | TRUE | TRUE
544 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.12 | TRUE | TRUE
545 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.12 | TRUE | TRUE
546 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
547 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.13 | FALSE | FALSE
548 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.13 | FALSE | FALSE
549 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
550 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
551 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
552 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
553 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
554 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.13 | TRUE | TRUE
555 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
556 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.13 | TRUE | TRUE
557 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
558 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.13 | TRUE | TRUE
559 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.13 | TRUE | TRUE
560 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.13 | TRUE | TRUE
561 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.13 | TRUE | TRUE
562 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
563 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.14 | FALSE | FALSE
564 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.14 | FALSE | FALSE
565 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
566 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
567 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
568 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
569 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
570 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.14 | TRUE | TRUE
571 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
572 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.14 | TRUE | TRUE
573 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
574 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.14 | TRUE | TRUE
575 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.14 | TRUE | TRUE
576 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.14 | TRUE | TRUE
577 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.14 | TRUE | TRUE
578 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
579 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.15 | FALSE | FALSE
580 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.15 | FALSE | FALSE
581 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
582 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
583 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
584 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
585 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
586 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.15 | TRUE | TRUE
587 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
588 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.15 | TRUE | TRUE
589 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
590 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.15 | TRUE | TRUE
591 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.15 | TRUE | TRUE
592 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.15 | TRUE | TRUE
593 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.15 | TRUE | TRUE
594 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
595 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.16 | FALSE | FALSE
596 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.16 | FALSE | FALSE
597 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
598 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
599 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
600 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
601 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
602 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.16 | TRUE | TRUE
603 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
604 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.16 | TRUE | TRUE
605 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
606 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.16 | TRUE | TRUE
607 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.16 | TRUE | TRUE
608 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.16 | TRUE | TRUE
609 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.16 | TRUE | TRUE
610 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
611 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.17 | FALSE | FALSE
612 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.17 | FALSE | FALSE
613 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
614 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
615 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
616 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
617 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
618 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.17 | TRUE | TRUE
619 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
620 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.17 | TRUE | TRUE
621 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
622 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.17 | TRUE | TRUE
623 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.17 | TRUE | TRUE
624 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.17 | TRUE | TRUE
625 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.17 | TRUE | TRUE
626 | lithium_ion_string | Lithium-Ion String Model | ID | Model identifier | uint16 |  | TRUE | TRUE
627 | lithium_ion_string | Lithium-Ion String Model | L | Model length | uint16 |  | TRUE | TRUE
628 | lithium_ion_string | Lithium-Ion String Model | Idx | Index of the string within the bank. | uint16 |  | TRUE | TRUE
629 | lithium_ion_string | Lithium-Ion String Model | NMod | Count of modules in the string. | uint16 |  | TRUE | TRUE
630 | lithium_ion_string | Lithium-Ion String Model | St | Current status of the string. | bitfield32 |  | TRUE | TRUE
632 | lithium_ion_string | Lithium-Ion String Model | ConFail |  | enum16 |  | FALSE | FALSE
633 | lithium_ion_string | Lithium-Ion String Model | NCellBal | Number of cells currently being balanced in the string. | uint16 |  | FALSE | FALSE
634 | lithium_ion_string | Lithium-Ion String Model | SoC | Battery string state of charge, expressed as a percentage. | uint16 |  | TRUE | TRUE
635 | lithium_ion_string | Lithium-Ion String Model | DoD | Depth of discharge for the string, expressed as a percentage. | uint16 |  | FALSE | FALSE
636 | lithium_ion_string | Lithium-Ion String Model | NCyc | Number of discharge cycles executed upon the string. | uint32 |  | FALSE | FALSE
638 | lithium_ion_string | Lithium-Ion String Model | SoH | Battery string state of health, expressed as a percentage. | uint16 |  | FALSE | TRUE
639 | lithium_ion_string | Lithium-Ion String Model | A | String current measurement. | int16 |  | TRUE | TRUE
640 | lithium_ion_string | Lithium-Ion String Model | V | String voltage measurement. | uint16 |  | FALSE | TRUE
641 | lithium_ion_string | Lithium-Ion String Model | CellVMax | Maximum voltage for all cells in the string. | uint16 |  | TRUE | TRUE
642 | lithium_ion_string | Lithium-Ion String Model | CellVMaxMod | Module containing the cell with maximum cell voltage. | uint16 |  | FALSE | FALSE
643 | lithium_ion_string | Lithium-Ion String Model | CellVMin | Minimum voltage for all cells in the string. | uint16 |  | TRUE | TRUE
644 | lithium_ion_string | Lithium-Ion String Model | CellVMinMod | Module containing the cell with minimum cell voltage. | uint16 |  | FALSE | FALSE
645 | lithium_ion_string | Lithium-Ion String Model | CellVAvg | Average voltage for all cells in the string. | uint16 |  | TRUE | TRUE
646 | lithium_ion_string | Lithium-Ion String Model | ModTmpMax | Maximum temperature for all modules in the string. | int16 |  | TRUE | TRUE
647 | lithium_ion_string | Lithium-Ion String Model | ModTmpMaxMod | Module with the maximum temperature. | uint16 |  | TRUE | TRUE
648 | lithium_ion_string | Lithium-Ion String Model | ModTmpMin | Minimum temperature for all modules in the string. | int16 |  | TRUE | TRUE
649 | lithium_ion_string | Lithium-Ion String Model | ModTmpMinMod | Module with the minimum temperature. | uint16 |  | TRUE | TRUE
650 | lithium_ion_string | Lithium-Ion String Model | ModTmpAvg | Average temperature for all modules in the string. | int16 |  | TRUE | TRUE
651 | lithium_ion_string | Lithium-Ion String Model | Pad1 | Pad register. | pad |  | TRUE | TRUE
652 | lithium_ion_string | Lithium-Ion String Model | ConSt | Status of the contactor(s) for the string. | bitfield32 |  | FALSE | FALSE
654 | lithium_ion_string | Lithium-Ion String Model | Evt1 | Alarms, warnings and status values. Bit flags. | bitfield32 |  | TRUE | TRUE
656 | lithium_ion_string | Lithium-Ion String Model | Evt2 | Alarms, warnings and status values. Bit flags. | bitfield32 |  | FALSE | FALSE
658 | lithium_ion_string | Lithium-Ion String Model | EvtVnd1 | Vendor defined events. | bitfield32 |  | FALSE | FALSE
660 | lithium_ion_string | Lithium-Ion String Model | EvtVnd2 | Vendor defined events. | bitfield32 |  | FALSE | FALSE
662 | lithium_ion_string | Lithium-Ion String Model | SetEna | Enables and disables the string. Should reset to 0 upon completion. | enum16 |  | FALSE | FALSE
663 | lithium_ion_string | Lithium-Ion String Model | SetCon | Connects and disconnects the string. | enum16 |  | FALSE | FALSE
664 | lithium_ion_string | Lithium-Ion String Model | SoC_SF | Scale factor for string state of charge. | sunssf |  | TRUE | TRUE
665 | lithium_ion_string | Lithium-Ion String Model | SoH_SF | Scale factor for string state of health. | sunssf |  | FALSE | TRUE
666 | lithium_ion_string | Lithium-Ion String Model | DoD_SF | Scale factor for string depth of discharge. | sunssf |  | FALSE | FALSE
667 | lithium_ion_string | Lithium-Ion String Model | A_SF | Scale factor for string current. | sunssf |  | TRUE | TRUE
668 | lithium_ion_string | Lithium-Ion String Model | V_SF | Scale factor for string voltage. | sunssf |  | FALSE | TRUE
669 | lithium_ion_string | Lithium-Ion String Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
670 | lithium_ion_string | Lithium-Ion String Model | ModTmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
671 | lithium_ion_string | Lithium-Ion String Model | Pad2 | Pad register. | pad |  | TRUE | TRUE
672 | lithium_ion_string | Lithium-Ion String Model | Pad3 | Pad register. | pad |  | TRUE | TRUE
673 | lithium_ion_string | Lithium-Ion String Model | Pad4 | Pad register. | pad |  | TRUE | TRUE
674 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
675 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.0 | FALSE | FALSE
676 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.0 | FALSE | FALSE
677 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
678 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
679 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
680 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
681 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
682 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
683 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
684 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
685 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
686 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
687 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
688 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
689 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
690 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
691 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.1 | FALSE | FALSE
692 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.1 | FALSE | FALSE
693 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
694 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
695 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
696 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
697 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
698 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
699 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
700 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
701 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
702 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
703 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
704 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
705 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
706 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
707 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.2 | FALSE | FALSE
708 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.2 | FALSE | FALSE
709 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
710 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
711 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
712 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
713 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
714 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
715 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
716 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
717 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
718 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
719 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
720 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
721 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
722 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
723 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.3 | FALSE | FALSE
724 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.3 | FALSE | FALSE
725 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
726 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
727 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
728 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
729 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
730 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
731 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
732 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
733 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
734 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
735 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
736 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
737 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
738 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
739 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.4 | FALSE | FALSE
740 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.4 | FALSE | FALSE
741 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
742 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
743 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
744 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
745 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
746 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.4 | TRUE | TRUE
747 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
748 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.4 | TRUE | TRUE
749 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
750 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.4 | TRUE | TRUE
751 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.4 | TRUE | TRUE
752 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.4 | TRUE | TRUE
753 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.4 | TRUE | TRUE
754 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
755 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.5 | FALSE | FALSE
756 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.5 | FALSE | FALSE
757 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
758 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
759 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
760 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
761 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
762 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.5 | TRUE | TRUE
763 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
764 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.5 | TRUE | TRUE
765 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
766 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.5 | TRUE | TRUE
767 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.5 | TRUE | TRUE
768 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.5 | TRUE | TRUE
769 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.5 | TRUE | TRUE
770 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
771 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.6 | FALSE | FALSE
772 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.6 | FALSE | FALSE
773 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
774 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
775 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
776 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
777 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
778 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.6 | TRUE | TRUE
779 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
780 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.6 | TRUE | TRUE
781 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
782 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.6 | TRUE | TRUE
783 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.6 | TRUE | TRUE
784 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.6 | TRUE | TRUE
785 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.6 | TRUE | TRUE
786 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
787 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.7 | FALSE | FALSE
788 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.7 | FALSE | FALSE
789 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
790 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
791 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
792 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
793 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
794 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.7 | TRUE | TRUE
795 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
796 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.7 | TRUE | TRUE
797 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
798 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.7 | TRUE | TRUE
799 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.7 | TRUE | TRUE
800 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.7 | TRUE | TRUE
801 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.7 | TRUE | TRUE
802 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
803 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.8 | FALSE | FALSE
804 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.8 | FALSE | FALSE
805 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
806 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
807 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
808 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
809 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
810 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.8 | TRUE | TRUE
811 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
812 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.8 | TRUE | TRUE
813 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
814 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.8 | TRUE | TRUE
815 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.8 | TRUE | TRUE
816 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.8 | TRUE | TRUE
817 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.8 | TRUE | TRUE
818 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
819 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.9 | FALSE | FALSE
820 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.9 | FALSE | FALSE
821 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
822 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
823 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
824 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
825 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
826 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.9 | TRUE | TRUE
827 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
828 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.9 | TRUE | TRUE
829 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
830 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.9 | TRUE | TRUE
831 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.9 | TRUE | TRUE
832 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.9 | TRUE | TRUE
833 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.9 | TRUE | TRUE
834 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
835 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.10 | FALSE | FALSE
836 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.10 | FALSE | FALSE
837 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
838 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
839 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
840 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
841 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
842 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.10 | TRUE | TRUE
843 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
844 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.10 | TRUE | TRUE
845 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
846 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.10 | TRUE | TRUE
847 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.10 | TRUE | TRUE
848 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.10 | TRUE | TRUE
849 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.10 | TRUE | TRUE
850 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
851 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.11 | FALSE | FALSE
852 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.11 | FALSE | FALSE
853 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
854 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
855 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
856 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
857 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
858 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.11 | TRUE | TRUE
859 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
860 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.11 | TRUE | TRUE
861 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
862 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.11 | TRUE | TRUE
863 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.11 | TRUE | TRUE
864 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.11 | TRUE | TRUE
865 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.11 | TRUE | TRUE
866 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
867 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.12 | FALSE | FALSE
868 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.12 | FALSE | FALSE
869 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
870 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
871 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
872 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
873 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
874 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.12 | TRUE | TRUE
875 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
876 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.12 | TRUE | TRUE
877 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
878 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.12 | TRUE | TRUE
879 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.12 | TRUE | TRUE
880 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.12 | TRUE | TRUE
881 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.12 | TRUE | TRUE
882 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
883 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.13 | FALSE | FALSE
884 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.13 | FALSE | FALSE
885 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
886 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
887 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
888 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
889 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
890 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.13 | TRUE | TRUE
891 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
892 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.13 | TRUE | TRUE
893 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
894 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.13 | TRUE | TRUE
895 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.13 | TRUE | TRUE
896 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.13 | TRUE | TRUE
897 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.13 | TRUE | TRUE
898 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
899 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.14 | FALSE | FALSE
900 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.14 | FALSE | FALSE
901 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
902 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
903 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
904 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
905 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
906 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.14 | TRUE | TRUE
907 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
908 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.14 | TRUE | TRUE
909 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
910 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.14 | TRUE | TRUE
911 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.14 | TRUE | TRUE
912 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.14 | TRUE | TRUE
913 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.14 | TRUE | TRUE
914 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
915 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.15 | FALSE | FALSE
916 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.15 | FALSE | FALSE
917 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
918 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
919 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
920 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
921 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
922 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.15 | TRUE | TRUE
923 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
924 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.15 | TRUE | TRUE
925 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
926 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.15 | TRUE | TRUE
927 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.15 | TRUE | TRUE
928 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.15 | TRUE | TRUE
929 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.15 | TRUE | TRUE
930 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
931 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.16 | FALSE | FALSE
932 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.16 | FALSE | FALSE
933 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
934 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
935 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
936 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
937 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
938 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.16 | TRUE | TRUE
939 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
940 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.16 | TRUE | TRUE
941 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
942 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.16 | TRUE | TRUE
943 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.16 | TRUE | TRUE
944 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.16 | TRUE | TRUE
945 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.16 | TRUE | TRUE
946 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
947 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.17 | FALSE | FALSE
948 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.17 | FALSE | FALSE
949 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
950 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
951 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
952 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
953 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
954 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.17 | TRUE | TRUE
955 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
956 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.17 | TRUE | TRUE
957 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
958 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.17 | TRUE | TRUE
959 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.17 | TRUE | TRUE
960 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.17 | TRUE | TRUE
961 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.17 | TRUE | TRUE
962 | lithium_ion_string | Lithium-Ion String Model | ID | Model identifier | uint16 |  | TRUE | TRUE
963 | lithium_ion_string | Lithium-Ion String Model | L | Model length | uint16 |  | TRUE | TRUE
964 | lithium_ion_string | Lithium-Ion String Model | Idx | Index of the string within the bank. | uint16 |  | TRUE | TRUE
965 | lithium_ion_string | Lithium-Ion String Model | NMod | Count of modules in the string. | uint16 |  | TRUE | TRUE
966 | lithium_ion_string | Lithium-Ion String Model | St | Current status of the string. | bitfield32 |  | TRUE | TRUE
968 | lithium_ion_string | Lithium-Ion String Model | ConFail |  | enum16 |  | FALSE | FALSE
969 | lithium_ion_string | Lithium-Ion String Model | NCellBal | Number of cells currently being balanced in the string. | uint16 |  | FALSE | FALSE
970 | lithium_ion_string | Lithium-Ion String Model | SoC | Battery string state of charge, expressed as a percentage. | uint16 |  | TRUE | TRUE
971 | lithium_ion_string | Lithium-Ion String Model | DoD | Depth of discharge for the string, expressed as a percentage. | uint16 |  | FALSE | FALSE
972 | lithium_ion_string | Lithium-Ion String Model | NCyc | Number of discharge cycles executed upon the string. | uint32 |  | FALSE | FALSE
974 | lithium_ion_string | Lithium-Ion String Model | SoH | Battery string state of health, expressed as a percentage. | uint16 |  | FALSE | TRUE
975 | lithium_ion_string | Lithium-Ion String Model | A | String current measurement. | int16 |  | TRUE | TRUE
976 | lithium_ion_string | Lithium-Ion String Model | V | String voltage measurement. | uint16 |  | FALSE | TRUE
977 | lithium_ion_string | Lithium-Ion String Model | CellVMax | Maximum voltage for all cells in the string. | uint16 |  | TRUE | TRUE
978 | lithium_ion_string | Lithium-Ion String Model | CellVMaxMod | Module containing the cell with maximum cell voltage. | uint16 |  | FALSE | FALSE
979 | lithium_ion_string | Lithium-Ion String Model | CellVMin | Minimum voltage for all cells in the string. | uint16 |  | TRUE | TRUE
980 | lithium_ion_string | Lithium-Ion String Model | CellVMinMod | Module containing the cell with minimum cell voltage. | uint16 |  | FALSE | FALSE
981 | lithium_ion_string | Lithium-Ion String Model | CellVAvg | Average voltage for all cells in the string. | uint16 |  | TRUE | TRUE
982 | lithium_ion_string | Lithium-Ion String Model | ModTmpMax | Maximum temperature for all modules in the string. | int16 |  | TRUE | TRUE
983 | lithium_ion_string | Lithium-Ion String Model | ModTmpMaxMod | Module with the maximum temperature. | uint16 |  | TRUE | TRUE
984 | lithium_ion_string | Lithium-Ion String Model | ModTmpMin | Minimum temperature for all modules in the string. | int16 |  | TRUE | TRUE
985 | lithium_ion_string | Lithium-Ion String Model | ModTmpMinMod | Module with the minimum temperature. | uint16 |  | TRUE | TRUE
986 | lithium_ion_string | Lithium-Ion String Model | ModTmpAvg | Average temperature for all modules in the string. | int16 |  | TRUE | TRUE
987 | lithium_ion_string | Lithium-Ion String Model | Pad1 | Pad register. | pad |  | TRUE | TRUE
988 | lithium_ion_string | Lithium-Ion String Model | ConSt | Status of the contactor(s) for the string. | bitfield32 |  | FALSE | FALSE
990 | lithium_ion_string | Lithium-Ion String Model | Evt1 | Alarms, warnings and status values. Bit flags. | bitfield32 |  | TRUE | TRUE
992 | lithium_ion_string | Lithium-Ion String Model | Evt2 | Alarms, warnings and status values. Bit flags. | bitfield32 |  | FALSE | FALSE
994 | lithium_ion_string | Lithium-Ion String Model | EvtVnd1 | Vendor defined events. | bitfield32 |  | FALSE | FALSE
996 | lithium_ion_string | Lithium-Ion String Model | EvtVnd2 | Vendor defined events. | bitfield32 |  | FALSE | FALSE
998 | lithium_ion_string | Lithium-Ion String Model | SetEna | Enables and disables the string. Should reset to 0 upon completion. | enum16 |  | FALSE | FALSE
999 | lithium_ion_string | Lithium-Ion String Model | SetCon | Connects and disconnects the string. | enum16 |  | FALSE | FALSE
1000 | lithium_ion_string | Lithium-Ion String Model | SoC_SF | Scale factor for string state of charge. | sunssf |  | TRUE | TRUE
1001 | lithium_ion_string | Lithium-Ion String Model | SoH_SF | Scale factor for string state of health. | sunssf |  | FALSE | TRUE
1002 | lithium_ion_string | Lithium-Ion String Model | DoD_SF | Scale factor for string depth of discharge. | sunssf |  | FALSE | FALSE
1003 | lithium_ion_string | Lithium-Ion String Model | A_SF | Scale factor for string current. | sunssf |  | TRUE | TRUE
1004 | lithium_ion_string | Lithium-Ion String Model | V_SF | Scale factor for string voltage. | sunssf |  | FALSE | TRUE
1005 | lithium_ion_string | Lithium-Ion String Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
1006 | lithium_ion_string | Lithium-Ion String Model | ModTmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
1007 | lithium_ion_string | Lithium-Ion String Model | Pad2 | Pad register. | pad |  | TRUE | TRUE
1008 | lithium_ion_string | Lithium-Ion String Model | Pad3 | Pad register. | pad |  | TRUE | TRUE
1009 | lithium_ion_string | Lithium-Ion String Model | Pad4 | Pad register. | pad |  | TRUE | TRUE
1010 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
1011 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.0 | FALSE | FALSE
1012 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.0 | FALSE | FALSE
1013 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
1014 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
1015 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
1016 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
1017 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
1018 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
1019 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
1020 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
1021 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
1022 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
1023 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
1024 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
1025 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
1026 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
1027 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.1 | FALSE | FALSE
1028 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.1 | FALSE | FALSE
1029 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
1030 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
1031 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
1032 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
1033 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
1034 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
1035 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
1036 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
1037 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
1038 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
1039 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
1040 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
1041 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
1042 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
1043 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.2 | FALSE | FALSE
1044 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.2 | FALSE | FALSE
1045 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
1046 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
1047 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
1048 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
1049 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
1050 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
1051 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
1052 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
1053 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
1054 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
1055 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
1056 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
1057 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
1058 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
1059 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.3 | FALSE | FALSE
1060 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.3 | FALSE | FALSE
1061 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
1062 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
1063 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
1064 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
1065 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
1066 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
1067 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
1068 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
1069 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
1070 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
1071 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
1072 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
1073 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
1074 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
1075 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.4 | FALSE | FALSE
1076 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.4 | FALSE | FALSE
1077 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
1078 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
1079 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
1080 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
1081 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
1082 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.4 | TRUE | TRUE
1083 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
1084 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.4 | TRUE | TRUE
1085 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
1086 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.4 | TRUE | TRUE
1087 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.4 | TRUE | TRUE
1088 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.4 | TRUE | TRUE
1089 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.4 | TRUE | TRUE
1090 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
1091 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.5 | FALSE | FALSE
1092 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.5 | FALSE | FALSE
1093 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
1094 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
1095 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
1096 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
1097 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
1098 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.5 | TRUE | TRUE
1099 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
1100 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.5 | TRUE | TRUE
1101 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
1102 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.5 | TRUE | TRUE
1103 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.5 | TRUE | TRUE
1104 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.5 | TRUE | TRUE
1105 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.5 | TRUE | TRUE
1106 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
1107 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.6 | FALSE | FALSE
1108 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.6 | FALSE | FALSE
1109 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
1110 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
1111 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
1112 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
1113 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
1114 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.6 | TRUE | TRUE
1115 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
1116 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.6 | TRUE | TRUE
1117 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
1118 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.6 | TRUE | TRUE
1119 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.6 | TRUE | TRUE
1120 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.6 | TRUE | TRUE
1121 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.6 | TRUE | TRUE
1122 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
1123 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.7 | FALSE | FALSE
1124 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.7 | FALSE | FALSE
1125 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
1126 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
1127 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
1128 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
1129 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
1130 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.7 | TRUE | TRUE
1131 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
1132 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.7 | TRUE | TRUE
1133 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
1134 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.7 | TRUE | TRUE
1135 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.7 | TRUE | TRUE
1136 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.7 | TRUE | TRUE
1137 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.7 | TRUE | TRUE
1138 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
1139 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.8 | FALSE | FALSE
1140 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.8 | FALSE | FALSE
1141 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
1142 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
1143 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
1144 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
1145 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
1146 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.8 | TRUE | TRUE
1147 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
1148 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.8 | TRUE | TRUE
1149 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
1150 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.8 | TRUE | TRUE
1151 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.8 | TRUE | TRUE
1152 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.8 | TRUE | TRUE
1153 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.8 | TRUE | TRUE
1154 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
1155 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.9 | FALSE | FALSE
1156 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.9 | FALSE | FALSE
1157 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
1158 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
1159 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
1160 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
1161 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
1162 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.9 | TRUE | TRUE
1163 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
1164 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.9 | TRUE | TRUE
1165 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
1166 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.9 | TRUE | TRUE
1167 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.9 | TRUE | TRUE
1168 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.9 | TRUE | TRUE
1169 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.9 | TRUE | TRUE
1170 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
1171 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.10 | FALSE | FALSE
1172 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.10 | FALSE | FALSE
1173 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
1174 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
1175 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
1176 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
1177 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
1178 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.10 | TRUE | TRUE
1179 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
1180 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.10 | TRUE | TRUE
1181 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
1182 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.10 | TRUE | TRUE
1183 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.10 | TRUE | TRUE
1184 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.10 | TRUE | TRUE
1185 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.10 | TRUE | TRUE
1186 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
1187 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.11 | FALSE | FALSE
1188 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.11 | FALSE | FALSE
1189 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
1190 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
1191 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
1192 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
1193 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
1194 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.11 | TRUE | TRUE
1195 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
1196 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.11 | TRUE | TRUE
1197 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
1198 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.11 | TRUE | TRUE
1199 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.11 | TRUE | TRUE
1200 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.11 | TRUE | TRUE
1201 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.11 | TRUE | TRUE
1202 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
1203 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.12 | FALSE | FALSE
1204 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.12 | FALSE | FALSE
1205 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
1206 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
1207 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
1208 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
1209 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
1210 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.12 | TRUE | TRUE
1211 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
1212 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.12 | TRUE | TRUE
1213 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
1214 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.12 | TRUE | TRUE
1215 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.12 | TRUE | TRUE
1216 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.12 | TRUE | TRUE
1217 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.12 | TRUE | TRUE
1218 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
1219 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.13 | FALSE | FALSE
1220 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.13 | FALSE | FALSE
1221 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
1222 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
1223 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
1224 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
1225 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
1226 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.13 | TRUE | TRUE
1227 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
1228 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.13 | TRUE | TRUE
1229 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
1230 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.13 | TRUE | TRUE
1231 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.13 | TRUE | TRUE
1232 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.13 | TRUE | TRUE
1233 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.13 | TRUE | TRUE
1234 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
1235 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.14 | FALSE | FALSE
1236 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.14 | FALSE | FALSE
1237 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
1238 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
1239 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
1240 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
1241 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
1242 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.14 | TRUE | TRUE
1243 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
1244 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.14 | TRUE | TRUE
1245 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
1246 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.14 | TRUE | TRUE
1247 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.14 | TRUE | TRUE
1248 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.14 | TRUE | TRUE
1249 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.14 | TRUE | TRUE
1250 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
1251 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.15 | FALSE | FALSE
1252 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.15 | FALSE | FALSE
1253 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
1254 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
1255 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
1256 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
1257 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
1258 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.15 | TRUE | TRUE
1259 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
1260 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.15 | TRUE | TRUE
1261 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
1262 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.15 | TRUE | TRUE
1263 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.15 | TRUE | TRUE
1264 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.15 | TRUE | TRUE
1265 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.15 | TRUE | TRUE
1266 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
1267 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.16 | FALSE | FALSE
1268 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.16 | FALSE | FALSE
1269 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
1270 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
1271 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
1272 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
1273 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
1274 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.16 | TRUE | TRUE
1275 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
1276 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.16 | TRUE | TRUE
1277 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
1278 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.16 | TRUE | TRUE
1279 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.16 | TRUE | TRUE
1280 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.16 | TRUE | TRUE
1281 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.16 | TRUE | TRUE
1282 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
1283 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.17 | FALSE | FALSE
1284 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.17 | FALSE | FALSE
1285 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
1286 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
1287 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
1288 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
1289 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
1290 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.17 | TRUE | TRUE
1291 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
1292 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.17 | TRUE | TRUE
1293 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
1294 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.17 | TRUE | TRUE
1295 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.17 | TRUE | TRUE
1296 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.17 | TRUE | TRUE
1297 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.17 | TRUE | TRUE
1298 | lithium_ion_string | Lithium-Ion String Model | ID | Model identifier | uint16 |  | TRUE | TRUE
1299 | lithium_ion_string | Lithium-Ion String Model | L | Model length | uint16 |  | TRUE | TRUE
1300 | lithium_ion_string | Lithium-Ion String Model | Idx | Index of the string within the bank. | uint16 |  | TRUE | TRUE
1301 | lithium_ion_string | Lithium-Ion String Model | NMod | Count of modules in the string. | uint16 |  | TRUE | TRUE
1302 | lithium_ion_string | Lithium-Ion String Model | St | Current status of the string. | bitfield32 |  | TRUE | TRUE
1304 | lithium_ion_string | Lithium-Ion String Model | ConFail |  | enum16 |  | FALSE | FALSE
1305 | lithium_ion_string | Lithium-Ion String Model | NCellBal | Number of cells currently being balanced in the string. | uint16 |  | FALSE | FALSE
1306 | lithium_ion_string | Lithium-Ion String Model | SoC | Battery string state of charge, expressed as a percentage. | uint16 |  | TRUE | TRUE
1307 | lithium_ion_string | Lithium-Ion String Model | DoD | Depth of discharge for the string, expressed as a percentage. | uint16 |  | FALSE | FALSE
1308 | lithium_ion_string | Lithium-Ion String Model | NCyc | Number of discharge cycles executed upon the string. | uint32 |  | FALSE | FALSE
1310 | lithium_ion_string | Lithium-Ion String Model | SoH | Battery string state of health, expressed as a percentage. | uint16 |  | FALSE | TRUE
1311 | lithium_ion_string | Lithium-Ion String Model | A | String current measurement. | int16 |  | TRUE | TRUE
1312 | lithium_ion_string | Lithium-Ion String Model | V | String voltage measurement. | uint16 |  | FALSE | TRUE
1313 | lithium_ion_string | Lithium-Ion String Model | CellVMax | Maximum voltage for all cells in the string. | uint16 |  | TRUE | TRUE
1314 | lithium_ion_string | Lithium-Ion String Model | CellVMaxMod | Module containing the cell with maximum cell voltage. | uint16 |  | FALSE | FALSE
1315 | lithium_ion_string | Lithium-Ion String Model | CellVMin | Minimum voltage for all cells in the string. | uint16 |  | TRUE | TRUE
1316 | lithium_ion_string | Lithium-Ion String Model | CellVMinMod | Module containing the cell with minimum cell voltage. | uint16 |  | FALSE | FALSE
1317 | lithium_ion_string | Lithium-Ion String Model | CellVAvg | Average voltage for all cells in the string. | uint16 |  | TRUE | TRUE
1318 | lithium_ion_string | Lithium-Ion String Model | ModTmpMax | Maximum temperature for all modules in the string. | int16 |  | TRUE | TRUE
1319 | lithium_ion_string | Lithium-Ion String Model | ModTmpMaxMod | Module with the maximum temperature. | uint16 |  | TRUE | TRUE
1320 | lithium_ion_string | Lithium-Ion String Model | ModTmpMin | Minimum temperature for all modules in the string. | int16 |  | TRUE | TRUE
1321 | lithium_ion_string | Lithium-Ion String Model | ModTmpMinMod | Module with the minimum temperature. | uint16 |  | TRUE | TRUE
1322 | lithium_ion_string | Lithium-Ion String Model | ModTmpAvg | Average temperature for all modules in the string. | int16 |  | TRUE | TRUE
1323 | lithium_ion_string | Lithium-Ion String Model | Pad1 | Pad register. | pad |  | TRUE | TRUE
1324 | lithium_ion_string | Lithium-Ion String Model | ConSt | Status of the contactor(s) for the string. | bitfield32 |  | FALSE | FALSE
1326 | lithium_ion_string | Lithium-Ion String Model | Evt1 | Alarms, warnings and status values. Bit flags. | bitfield32 |  | TRUE | TRUE
1328 | lithium_ion_string | Lithium-Ion String Model | Evt2 | Alarms, warnings and status values. Bit flags. | bitfield32 |  | FALSE | FALSE
1330 | lithium_ion_string | Lithium-Ion String Model | EvtVnd1 | Vendor defined events. | bitfield32 |  | FALSE | FALSE
1332 | lithium_ion_string | Lithium-Ion String Model | EvtVnd2 | Vendor defined events. | bitfield32 |  | FALSE | FALSE
1334 | lithium_ion_string | Lithium-Ion String Model | SetEna | Enables and disables the string. Should reset to 0 upon completion. | enum16 |  | FALSE | FALSE
1335 | lithium_ion_string | Lithium-Ion String Model | SetCon | Connects and disconnects the string. | enum16 |  | FALSE | FALSE
1336 | lithium_ion_string | Lithium-Ion String Model | SoC_SF | Scale factor for string state of charge. | sunssf |  | TRUE | TRUE
1337 | lithium_ion_string | Lithium-Ion String Model | SoH_SF | Scale factor for string state of health. | sunssf |  | FALSE | TRUE
1338 | lithium_ion_string | Lithium-Ion String Model | DoD_SF | Scale factor for string depth of discharge. | sunssf |  | FALSE | FALSE
1339 | lithium_ion_string | Lithium-Ion String Model | A_SF | Scale factor for string current. | sunssf |  | TRUE | TRUE
1340 | lithium_ion_string | Lithium-Ion String Model | V_SF | Scale factor for string voltage. | sunssf |  | FALSE | TRUE
1341 | lithium_ion_string | Lithium-Ion String Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
1342 | lithium_ion_string | Lithium-Ion String Model | ModTmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
1343 | lithium_ion_string | Lithium-Ion String Model | Pad2 | Pad register. | pad |  | TRUE | TRUE
1344 | lithium_ion_string | Lithium-Ion String Model | Pad3 | Pad register. | pad |  | TRUE | TRUE
1345 | lithium_ion_string | Lithium-Ion String Model | Pad4 | Pad register. | pad |  | TRUE | TRUE
1346 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
1347 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.0 | FALSE | FALSE
1348 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.0 | FALSE | FALSE
1349 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
1350 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
1351 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
1352 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
1353 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.0 | TRUE | TRUE
1354 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
1355 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
1356 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
1357 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.0 | FALSE | TRUE
1358 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.0 | TRUE | TRUE
1359 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
1360 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
1361 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.0 | TRUE | TRUE
1362 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
1363 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.1 | FALSE | FALSE
1364 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.1 | FALSE | FALSE
1365 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
1366 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
1367 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
1368 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
1369 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.1 | TRUE | TRUE
1370 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
1371 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
1372 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
1373 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.1 | FALSE | TRUE
1374 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.1 | TRUE | TRUE
1375 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
1376 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
1377 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.1 | TRUE | TRUE
1378 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
1379 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.2 | FALSE | FALSE
1380 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.2 | FALSE | FALSE
1381 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
1382 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
1383 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
1384 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
1385 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.2 | TRUE | TRUE
1386 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
1387 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
1388 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
1389 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.2 | FALSE | TRUE
1390 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.2 | TRUE | TRUE
1391 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
1392 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
1393 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.2 | TRUE | TRUE
1394 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
1395 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.3 | FALSE | FALSE
1396 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.3 | FALSE | FALSE
1397 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
1398 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
1399 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
1400 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
1401 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.3 | TRUE | TRUE
1402 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
1403 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
1404 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
1405 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.3 | FALSE | TRUE
1406 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.3 | TRUE | TRUE
1407 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
1408 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
1409 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.3 | TRUE | TRUE
1410 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
1411 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.4 | FALSE | FALSE
1412 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.4 | FALSE | FALSE
1413 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
1414 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
1415 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
1416 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
1417 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.4 | TRUE | TRUE
1418 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.4 | TRUE | TRUE
1419 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
1420 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.4 | TRUE | TRUE
1421 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.4 | FALSE | TRUE
1422 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.4 | TRUE | TRUE
1423 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.4 | TRUE | TRUE
1424 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.4 | TRUE | TRUE
1425 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.4 | TRUE | TRUE
1426 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
1427 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.5 | FALSE | FALSE
1428 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.5 | FALSE | FALSE
1429 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
1430 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
1431 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
1432 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
1433 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.5 | TRUE | TRUE
1434 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.5 | TRUE | TRUE
1435 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
1436 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.5 | TRUE | TRUE
1437 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.5 | FALSE | TRUE
1438 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.5 | TRUE | TRUE
1439 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.5 | TRUE | TRUE
1440 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.5 | TRUE | TRUE
1441 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.5 | TRUE | TRUE
1442 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
1443 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.6 | FALSE | FALSE
1444 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.6 | FALSE | FALSE
1445 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
1446 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
1447 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
1448 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
1449 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.6 | TRUE | TRUE
1450 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.6 | TRUE | TRUE
1451 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
1452 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.6 | TRUE | TRUE
1453 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.6 | FALSE | TRUE
1454 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.6 | TRUE | TRUE
1455 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.6 | TRUE | TRUE
1456 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.6 | TRUE | TRUE
1457 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.6 | TRUE | TRUE
1458 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
1459 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.7 | FALSE | FALSE
1460 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.7 | FALSE | FALSE
1461 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
1462 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
1463 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
1464 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
1465 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.7 | TRUE | TRUE
1466 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.7 | TRUE | TRUE
1467 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
1468 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.7 | TRUE | TRUE
1469 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.7 | FALSE | TRUE
1470 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.7 | TRUE | TRUE
1471 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.7 | TRUE | TRUE
1472 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.7 | TRUE | TRUE
1473 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.7 | TRUE | TRUE
1474 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
1475 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.8 | FALSE | FALSE
1476 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.8 | FALSE | FALSE
1477 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
1478 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
1479 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
1480 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
1481 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.8 | TRUE | TRUE
1482 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.8 | TRUE | TRUE
1483 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
1484 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.8 | TRUE | TRUE
1485 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.8 | FALSE | TRUE
1486 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.8 | TRUE | TRUE
1487 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.8 | TRUE | TRUE
1488 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.8 | TRUE | TRUE
1489 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.8 | TRUE | TRUE
1490 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
1491 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.9 | FALSE | FALSE
1492 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.9 | FALSE | FALSE
1493 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
1494 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
1495 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
1496 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
1497 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.9 | TRUE | TRUE
1498 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.9 | TRUE | TRUE
1499 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
1500 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.9 | TRUE | TRUE
1501 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.9 | FALSE | TRUE
1502 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.9 | TRUE | TRUE
1503 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.9 | TRUE | TRUE
1504 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.9 | TRUE | TRUE
1505 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.9 | TRUE | TRUE
1506 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
1507 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.10 | FALSE | FALSE
1508 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.10 | FALSE | FALSE
1509 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
1510 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
1511 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
1512 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
1513 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.10 | TRUE | TRUE
1514 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.10 | TRUE | TRUE
1515 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
1516 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.10 | TRUE | TRUE
1517 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.10 | FALSE | TRUE
1518 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.10 | TRUE | TRUE
1519 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.10 | TRUE | TRUE
1520 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.10 | TRUE | TRUE
1521 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.10 | TRUE | TRUE
1522 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
1523 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.11 | FALSE | FALSE
1524 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.11 | FALSE | FALSE
1525 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
1526 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
1527 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
1528 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
1529 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.11 | TRUE | TRUE
1530 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.11 | TRUE | TRUE
1531 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
1532 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.11 | TRUE | TRUE
1533 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.11 | FALSE | TRUE
1534 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.11 | TRUE | TRUE
1535 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.11 | TRUE | TRUE
1536 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.11 | TRUE | TRUE
1537 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.11 | TRUE | TRUE
1538 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
1539 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.12 | FALSE | FALSE
1540 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.12 | FALSE | FALSE
1541 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
1542 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
1543 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
1544 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
1545 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.12 | TRUE | TRUE
1546 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.12 | TRUE | TRUE
1547 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
1548 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.12 | TRUE | TRUE
1549 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.12 | FALSE | TRUE
1550 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.12 | TRUE | TRUE
1551 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.12 | TRUE | TRUE
1552 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.12 | TRUE | TRUE
1553 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.12 | TRUE | TRUE
1554 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
1555 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.13 | FALSE | FALSE
1556 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.13 | FALSE | FALSE
1557 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
1558 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
1559 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
1560 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
1561 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.13 | TRUE | TRUE
1562 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.13 | TRUE | TRUE
1563 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
1564 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.13 | TRUE | TRUE
1565 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.13 | FALSE | TRUE
1566 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.13 | TRUE | TRUE
1567 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.13 | TRUE | TRUE
1568 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.13 | TRUE | TRUE
1569 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.13 | TRUE | TRUE
1570 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
1571 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.14 | FALSE | FALSE
1572 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.14 | FALSE | FALSE
1573 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
1574 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
1575 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
1576 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
1577 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.14 | TRUE | TRUE
1578 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.14 | TRUE | TRUE
1579 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
1580 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.14 | TRUE | TRUE
1581 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.14 | FALSE | TRUE
1582 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.14 | TRUE | TRUE
1583 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.14 | TRUE | TRUE
1584 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.14 | TRUE | TRUE
1585 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.14 | TRUE | TRUE
1586 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
1587 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.15 | FALSE | FALSE
1588 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.15 | FALSE | FALSE
1589 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
1590 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
1591 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
1592 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
1593 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.15 | TRUE | TRUE
1594 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.15 | TRUE | TRUE
1595 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
1596 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.15 | TRUE | TRUE
1597 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.15 | FALSE | TRUE
1598 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.15 | TRUE | TRUE
1599 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.15 | TRUE | TRUE
1600 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.15 | TRUE | TRUE
1601 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.15 | TRUE | TRUE
1602 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
1603 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.16 | FALSE | FALSE
1604 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.16 | FALSE | FALSE
1605 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
1606 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
1607 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
1608 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
1609 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.16 | TRUE | TRUE
1610 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.16 | TRUE | TRUE
1611 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
1612 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.16 | TRUE | TRUE
1613 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.16 | FALSE | TRUE
1614 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.16 | TRUE | TRUE
1615 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.16 | TRUE | TRUE
1616 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.16 | TRUE | TRUE
1617 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.16 | TRUE | TRUE
1618 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModNCell | Count of all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
1619 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoC | Module state of charge, expressed as a percentage. | uint16 | lithium_ion_string_module.17 | FALSE | FALSE
1620 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModSoH | Module state of health, expressed as a percentage. | uint16 | lithium_ion_string_module.17 | FALSE | FALSE
1621 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMax | Maximum voltage for all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
1622 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMaxCell | Cell with maximum voltage. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
1623 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMin | Minimum voltage for all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
1624 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVMinCell | Cell with minimum voltage. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
1625 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellVAvg | Average voltage for all cells in the module. | uint16 | lithium_ion_string_module.17 | TRUE | TRUE
1626 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMax | Maximum temperature for all cells in the module. | int16 | lithium_ion_string_module.17 | TRUE | TRUE
1627 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMaxCell | Cell with maximum temperature. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
1628 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMin | Minimum temperature for all cells in the module. | int16 | lithium_ion_string_module.17 | TRUE | TRUE
1629 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpMinCell | Cell with minimum temperature. | uint16 | lithium_ion_string_module.17 | FALSE | TRUE
1630 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.ModCellTmpAvg | Average temperature for all cells in the module. | int16 | lithium_ion_string_module.17 | TRUE | TRUE
1631 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad5 | Pad register. | pad | lithium_ion_string_module.17 | TRUE | TRUE
1632 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad6 | Pad register. | pad | lithium_ion_string_module.17 | TRUE | TRUE
1633 | lithium_ion_string | Lithium-Ion String Model | lithium_ion_string_module.Pad7 | Pad register. | pad | lithium_ion_string_module.17 | TRUE | TRUE
1634 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
1635 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
1636 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
1637 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
1638 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
1639 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
1640 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
1641 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
1642 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
1644 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
1645 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1646 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
1647 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1648 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
1649 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1650 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1651 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
1652 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1653 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
1654 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
1655 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
1656 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
1672 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
1673 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
1674 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
1675 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
1676 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
1677 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
1678 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
1679 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
1680 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
1682 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
1683 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
1684 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
1686 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
1687 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
1688 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
1690 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
1691 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
1692 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
1694 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
1695 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
1696 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
1698 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
1699 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
1700 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
1702 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
1703 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
1704 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
1706 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
1707 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
1708 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
1710 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
1711 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
1712 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
1714 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
1715 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
1716 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
1718 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
1719 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
1720 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
1722 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
1723 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
1724 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
1726 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
1727 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
1728 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
1730 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
1731 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
1732 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
1734 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
1735 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
1736 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
1738 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
1739 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
1740 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
1742 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
1743 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
1744 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
1745 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
1746 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
1747 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
1748 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
1749 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
1750 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
1752 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
1753 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1754 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
1755 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1756 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
1757 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1758 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1759 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
1760 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1761 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
1762 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
1763 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
1764 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
1780 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
1781 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
1782 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
1783 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
1784 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
1785 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
1786 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
1787 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
1788 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
1790 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
1791 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
1792 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
1794 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
1795 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
1796 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
1798 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
1799 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
1800 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
1802 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
1803 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
1804 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
1806 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
1807 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
1808 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
1810 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
1811 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
1812 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
1814 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
1815 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
1816 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
1818 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
1819 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
1820 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
1822 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
1823 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
1824 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
1826 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
1827 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
1828 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
1830 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
1831 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
1832 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
1834 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
1835 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
1836 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
1838 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
1839 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
1840 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
1842 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
1843 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
1844 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
1846 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
1847 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
1848 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
1850 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
1851 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
1852 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
1853 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
1854 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
1855 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
1856 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
1857 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
1858 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
1860 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
1861 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1862 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
1863 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1864 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
1865 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1866 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1867 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
1868 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1869 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
1870 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
1871 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
1872 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
1888 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
1889 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
1890 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
1891 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
1892 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
1893 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
1894 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
1895 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
1896 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
1898 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
1899 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
1900 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
1902 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
1903 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
1904 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
1906 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
1907 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
1908 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
1910 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
1911 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
1912 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
1914 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
1915 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
1916 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
1918 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
1919 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
1920 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
1922 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
1923 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
1924 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
1926 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
1927 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
1928 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
1930 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
1931 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
1932 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
1934 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
1935 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
1936 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
1938 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
1939 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
1940 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
1942 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
1943 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
1944 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
1946 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
1947 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
1948 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
1950 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
1951 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
1952 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
1954 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
1955 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
1956 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
1958 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
1959 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
1960 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
1961 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
1962 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
1963 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
1964 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
1965 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
1966 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
1968 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
1969 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1970 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
1971 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1972 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
1973 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
1974 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1975 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
1976 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
1977 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
1978 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
1979 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
1980 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
1996 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
1997 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
1998 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
1999 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
2000 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
2001 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
2002 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
2003 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
2004 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
2006 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
2007 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
2008 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
2010 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
2011 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
2012 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
2014 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
2015 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
2016 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
2018 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
2019 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
2020 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
2022 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
2023 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
2024 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
2026 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
2027 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
2028 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
2030 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
2031 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
2032 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
2034 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
2035 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
2036 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
2038 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
2039 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
2040 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
2042 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
2043 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
2044 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
2046 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
2047 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
2048 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
2050 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
2051 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
2052 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
2054 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
2055 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
2056 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
2058 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
2059 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
2060 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
2062 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
2063 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
2064 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
2066 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
2067 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
2068 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
2069 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
2070 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
2071 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
2072 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
2073 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
2074 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
2076 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
2077 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2078 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
2079 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2080 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
2081 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2082 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2083 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
2084 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2085 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
2086 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
2087 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
2088 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
2104 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
2105 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
2106 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
2107 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
2108 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
2109 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
2110 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
2111 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
2112 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
2114 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
2115 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
2116 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
2118 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
2119 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
2120 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
2122 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
2123 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
2124 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
2126 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
2127 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
2128 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
2130 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
2131 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
2132 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
2134 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
2135 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
2136 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
2138 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
2139 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
2140 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
2142 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
2143 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
2144 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
2146 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
2147 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
2148 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
2150 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
2151 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
2152 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
2154 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
2155 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
2156 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
2158 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
2159 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
2160 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
2162 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
2163 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
2164 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
2166 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
2167 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
2168 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
2170 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
2171 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
2172 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
2174 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
2175 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
2176 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
2177 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
2178 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
2179 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
2180 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
2181 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
2182 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
2184 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
2185 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2186 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
2187 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2188 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
2189 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2190 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2191 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
2192 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2193 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
2194 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
2195 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
2196 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
2212 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
2213 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
2214 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
2215 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
2216 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
2217 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
2218 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
2219 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
2220 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
2222 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
2223 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
2224 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
2226 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
2227 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
2228 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
2230 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
2231 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
2232 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
2234 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
2235 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
2236 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
2238 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
2239 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
2240 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
2242 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
2243 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
2244 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
2246 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
2247 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
2248 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
2250 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
2251 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
2252 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
2254 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
2255 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
2256 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
2258 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
2259 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
2260 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
2262 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
2263 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
2264 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
2266 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
2267 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
2268 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
2270 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
2271 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
2272 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
2274 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
2275 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
2276 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
2278 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
2279 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
2280 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
2282 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
2283 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
2284 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
2285 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
2286 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
2287 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
2288 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
2289 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
2290 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
2292 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
2293 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2294 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
2295 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2296 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
2297 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2298 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2299 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
2300 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2301 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
2302 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
2303 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
2304 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
2320 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
2321 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
2322 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
2323 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
2324 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
2325 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
2326 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
2327 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
2328 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
2330 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
2331 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
2332 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
2334 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
2335 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
2336 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
2338 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
2339 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
2340 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
2342 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
2343 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
2344 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
2346 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
2347 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
2348 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
2350 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
2351 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
2352 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
2354 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
2355 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
2356 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
2358 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
2359 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
2360 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
2362 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
2363 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
2364 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
2366 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
2367 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
2368 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
2370 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
2371 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
2372 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
2374 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
2375 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
2376 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
2378 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
2379 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
2380 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
2382 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
2383 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
2384 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
2386 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
2387 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
2388 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
2390 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
2391 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
2392 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
2393 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
2394 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
2395 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
2396 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
2397 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
2398 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
2400 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
2401 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2402 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
2403 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2404 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
2405 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2406 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2407 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
2408 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2409 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
2410 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
2411 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
2412 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
2428 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
2429 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
2430 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
2431 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
2432 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
2433 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
2434 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
2435 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
2436 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
2438 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
2439 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
2440 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
2442 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
2443 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
2444 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
2446 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
2447 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
2448 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
2450 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
2451 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
2452 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
2454 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
2455 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
2456 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
2458 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
2459 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
2460 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
2462 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
2463 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
2464 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
2466 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
2467 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
2468 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
2470 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
2471 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
2472 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
2474 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
2475 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
2476 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
2478 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
2479 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
2480 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
2482 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
2483 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
2484 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
2486 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
2487 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
2488 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
2490 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
2491 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
2492 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
2494 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
2495 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
2496 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
2498 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
2499 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
2500 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
2501 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
2502 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
2503 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
2504 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
2505 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
2506 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
2508 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
2509 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2510 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
2511 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2512 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
2513 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2514 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2515 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
2516 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2517 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
2518 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
2519 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
2520 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
2536 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
2537 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
2538 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
2539 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
2540 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
2541 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
2542 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
2543 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
2544 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
2546 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
2547 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
2548 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
2550 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
2551 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
2552 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
2554 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
2555 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
2556 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
2558 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
2559 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
2560 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
2562 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
2563 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
2564 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
2566 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
2567 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
2568 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
2570 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
2571 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
2572 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
2574 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
2575 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
2576 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
2578 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
2579 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
2580 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
2582 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
2583 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
2584 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
2586 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
2587 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
2588 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
2590 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
2591 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
2592 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
2594 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
2595 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
2596 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
2598 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
2599 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
2600 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
2602 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
2603 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
2604 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
2606 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
2607 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
2608 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
2609 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
2610 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
2611 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
2612 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
2613 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
2614 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
2616 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
2617 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2618 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
2619 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2620 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
2621 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2622 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2623 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
2624 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2625 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
2626 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
2627 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
2628 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
2644 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
2645 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
2646 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
2647 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
2648 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
2649 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
2650 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
2651 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
2652 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
2654 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
2655 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
2656 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
2658 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
2659 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
2660 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
2662 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
2663 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
2664 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
2666 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
2667 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
2668 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
2670 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
2671 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
2672 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
2674 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
2675 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
2676 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
2678 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
2679 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
2680 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
2682 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
2683 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
2684 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
2686 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
2687 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
2688 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
2690 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
2691 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
2692 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
2694 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
2695 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
2696 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
2698 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
2699 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
2700 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
2702 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
2703 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
2704 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
2706 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
2707 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
2708 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
2710 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
2711 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
2712 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
2714 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
2715 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
2716 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
2717 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
2718 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
2719 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
2720 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
2721 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
2722 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
2724 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
2725 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2726 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
2727 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2728 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
2729 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2730 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2731 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
2732 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2733 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
2734 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
2735 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
2736 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
2752 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
2753 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
2754 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
2755 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
2756 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
2757 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
2758 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
2759 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
2760 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
2762 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
2763 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
2764 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
2766 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
2767 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
2768 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
2770 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
2771 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
2772 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
2774 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
2775 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
2776 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
2778 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
2779 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
2780 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
2782 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
2783 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
2784 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
2786 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
2787 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
2788 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
2790 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
2791 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
2792 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
2794 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
2795 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
2796 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
2798 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
2799 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
2800 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
2802 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
2803 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
2804 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
2806 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
2807 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
2808 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
2810 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
2811 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
2812 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
2814 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
2815 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
2816 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
2818 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
2819 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
2820 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
2822 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
2823 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
2824 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
2825 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
2826 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
2827 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
2828 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
2829 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
2830 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
2832 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
2833 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2834 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
2835 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2836 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
2837 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2838 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2839 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
2840 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2841 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
2842 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
2843 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
2844 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
2860 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
2861 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
2862 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
2863 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
2864 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
2865 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
2866 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
2867 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
2868 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
2870 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
2871 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
2872 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
2874 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
2875 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
2876 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
2878 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
2879 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
2880 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
2882 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
2883 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
2884 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
2886 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
2887 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
2888 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
2890 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
2891 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
2892 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
2894 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
2895 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
2896 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
2898 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
2899 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
2900 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
2902 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
2903 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
2904 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
2906 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
2907 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
2908 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
2910 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
2911 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
2912 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
2914 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
2915 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
2916 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
2918 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
2919 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
2920 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
2922 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
2923 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
2924 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
2926 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
2927 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
2928 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
2930 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
2931 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
2932 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
2933 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
2934 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
2935 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
2936 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
2937 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
2938 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
2940 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
2941 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2942 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
2943 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2944 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
2945 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
2946 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2947 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
2948 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
2949 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
2950 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
2951 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
2952 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
2968 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
2969 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
2970 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
2971 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
2972 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
2973 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
2974 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
2975 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
2976 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
2978 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
2979 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
2980 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
2982 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
2983 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
2984 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
2986 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
2987 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
2988 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
2990 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
2991 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
2992 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
2994 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
2995 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
2996 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
2998 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
2999 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
3000 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
3002 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
3003 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
3004 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
3006 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
3007 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
3008 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
3010 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
3011 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
3012 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
3014 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
3015 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
3016 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
3018 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
3019 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
3020 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
3022 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
3023 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
3024 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
3026 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
3027 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
3028 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
3030 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
3031 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
3032 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
3034 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
3035 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
3036 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
3038 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
3039 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
3040 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
3041 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
3042 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
3043 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
3044 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
3045 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
3046 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
3048 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
3049 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3050 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
3051 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3052 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
3053 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3054 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3055 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
3056 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3057 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
3058 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
3059 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
3060 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
3076 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
3077 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
3078 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
3079 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
3080 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
3081 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
3082 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
3083 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
3084 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
3086 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
3087 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
3088 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
3090 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
3091 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
3092 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
3094 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
3095 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
3096 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
3098 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
3099 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
3100 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
3102 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
3103 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
3104 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
3106 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
3107 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
3108 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
3110 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
3111 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
3112 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
3114 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
3115 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
3116 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
3118 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
3119 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
3120 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
3122 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
3123 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
3124 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
3126 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
3127 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
3128 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
3130 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
3131 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
3132 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
3134 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
3135 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
3136 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
3138 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
3139 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
3140 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
3142 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
3143 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
3144 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
3146 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
3147 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
3148 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
3149 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
3150 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
3151 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
3152 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
3153 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
3154 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
3156 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
3157 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3158 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
3159 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3160 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
3161 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3162 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3163 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
3164 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3165 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
3166 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
3167 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
3168 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
3184 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
3185 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
3186 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
3187 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
3188 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
3189 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
3190 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
3191 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
3192 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
3194 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
3195 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
3196 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
3198 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
3199 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
3200 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
3202 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
3203 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
3204 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
3206 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
3207 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
3208 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
3210 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
3211 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
3212 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
3214 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
3215 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
3216 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
3218 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
3219 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
3220 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
3222 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
3223 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
3224 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
3226 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
3227 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
3228 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
3230 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
3231 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
3232 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
3234 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
3235 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
3236 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
3238 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
3239 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
3240 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
3242 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
3243 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
3244 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
3246 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
3247 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
3248 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
3250 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
3251 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
3252 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
3254 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
3255 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
3256 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
3257 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
3258 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
3259 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
3260 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
3261 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
3262 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
3264 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
3265 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3266 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
3267 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3268 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
3269 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3270 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3271 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
3272 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3273 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
3274 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
3275 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
3276 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
3292 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
3293 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
3294 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
3295 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
3296 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
3297 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
3298 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
3299 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
3300 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
3302 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
3303 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
3304 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
3306 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
3307 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
3308 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
3310 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
3311 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
3312 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
3314 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
3315 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
3316 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
3318 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
3319 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
3320 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
3322 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
3323 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
3324 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
3326 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
3327 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
3328 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
3330 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
3331 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
3332 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
3334 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
3335 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
3336 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
3338 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
3339 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
3340 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
3342 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
3343 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
3344 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
3346 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
3347 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
3348 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
3350 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
3351 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
3352 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
3354 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
3355 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
3356 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
3358 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
3359 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
3360 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
3362 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
3363 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
3364 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
3365 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
3366 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
3367 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
3368 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
3369 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
3370 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
3372 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
3373 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3374 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
3375 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3376 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
3377 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3378 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3379 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
3380 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3381 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
3382 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
3383 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
3384 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
3400 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
3401 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
3402 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
3403 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
3404 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
3405 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
3406 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
3407 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
3408 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
3410 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
3411 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
3412 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
3414 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
3415 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
3416 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
3418 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
3419 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
3420 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
3422 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
3423 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
3424 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
3426 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
3427 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
3428 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
3430 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
3431 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
3432 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
3434 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
3435 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
3436 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
3438 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
3439 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
3440 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
3442 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
3443 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
3444 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
3446 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
3447 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
3448 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
3450 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
3451 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
3452 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
3454 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
3455 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
3456 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
3458 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
3459 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
3460 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
3462 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
3463 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
3464 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
3466 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
3467 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
3468 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
3470 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
3471 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
3472 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
3473 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
3474 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
3475 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
3476 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
3477 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
3478 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
3480 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
3481 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3482 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
3483 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3484 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
3485 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3486 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3487 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
3488 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3489 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
3490 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
3491 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
3492 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
3508 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
3509 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
3510 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
3511 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
3512 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
3513 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
3514 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
3515 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
3516 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
3518 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
3519 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
3520 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
3522 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
3523 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
3524 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
3526 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
3527 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
3528 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
3530 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
3531 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
3532 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
3534 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
3535 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
3536 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
3538 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
3539 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
3540 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
3542 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
3543 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
3544 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
3546 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
3547 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
3548 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
3550 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
3551 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
3552 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
3554 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
3555 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
3556 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
3558 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
3559 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
3560 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
3562 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
3563 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
3564 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
3566 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
3567 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
3568 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
3570 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
3571 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
3572 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
3574 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
3575 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
3576 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
3578 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
3579 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
3580 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
3581 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
3582 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
3583 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
3584 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
3585 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
3586 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
3588 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
3589 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3590 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
3591 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3592 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
3593 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3594 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3595 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
3596 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3597 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
3598 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
3599 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
3600 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
3616 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
3617 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
3618 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
3619 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
3620 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
3621 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
3622 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
3623 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
3624 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
3626 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
3627 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
3628 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
3630 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
3631 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
3632 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
3634 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
3635 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
3636 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
3638 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
3639 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
3640 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
3642 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
3643 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
3644 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
3646 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
3647 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
3648 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
3650 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
3651 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
3652 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
3654 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
3655 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
3656 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
3658 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
3659 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
3660 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
3662 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
3663 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
3664 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
3666 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
3667 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
3668 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
3670 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
3671 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
3672 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
3674 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
3675 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
3676 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
3678 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
3679 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
3680 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
3682 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
3683 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
3684 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
3686 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
3687 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
3688 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
3689 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
3690 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
3691 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
3692 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
3693 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
3694 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
3696 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
3697 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3698 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
3699 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3700 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
3701 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3702 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3703 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
3704 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3705 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
3706 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
3707 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
3708 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
3724 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
3725 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
3726 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
3727 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
3728 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
3729 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
3730 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
3731 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
3732 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
3734 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
3735 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
3736 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
3738 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
3739 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
3740 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
3742 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
3743 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
3744 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
3746 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
3747 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
3748 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
3750 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
3751 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
3752 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
3754 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
3755 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
3756 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
3758 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
3759 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
3760 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
3762 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
3763 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
3764 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
3766 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
3767 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
3768 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
3770 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
3771 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
3772 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
3774 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
3775 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
3776 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
3778 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
3779 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
3780 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
3782 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
3783 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
3784 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
3786 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
3787 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
3788 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
3790 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
3791 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
3792 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
3794 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
3795 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
3796 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
3797 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
3798 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
3799 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
3800 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
3801 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
3802 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
3804 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
3805 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3806 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
3807 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3808 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
3809 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3810 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3811 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
3812 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3813 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
3814 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
3815 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
3816 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
3832 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
3833 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
3834 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
3835 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
3836 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
3837 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
3838 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
3839 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
3840 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
3842 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
3843 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
3844 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
3846 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
3847 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
3848 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
3850 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
3851 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
3852 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
3854 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
3855 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
3856 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
3858 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
3859 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
3860 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
3862 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
3863 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
3864 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
3866 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
3867 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
3868 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
3870 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
3871 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
3872 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
3874 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
3875 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
3876 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
3878 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
3879 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
3880 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
3882 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
3883 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
3884 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
3886 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
3887 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
3888 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
3890 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
3891 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
3892 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
3894 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
3895 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
3896 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
3898 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
3899 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
3900 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
3902 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
3903 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
3904 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
3905 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
3906 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
3907 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
3908 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
3909 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
3910 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
3912 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
3913 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3914 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
3915 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3916 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
3917 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
3918 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3919 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
3920 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
3921 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
3922 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
3923 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
3924 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
3940 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
3941 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
3942 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
3943 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
3944 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
3945 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
3946 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
3947 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
3948 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
3950 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
3951 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
3952 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
3954 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
3955 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
3956 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
3958 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
3959 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
3960 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
3962 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
3963 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
3964 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
3966 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
3967 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
3968 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
3970 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
3971 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
3972 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
3974 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
3975 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
3976 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
3978 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
3979 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
3980 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
3982 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
3983 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
3984 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
3986 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
3987 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
3988 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
3990 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
3991 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
3992 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
3994 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
3995 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
3996 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
3998 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
3999 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
4000 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
4002 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
4003 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
4004 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
4006 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
4007 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
4008 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
4010 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
4011 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
4012 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
4013 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
4014 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
4015 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
4016 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
4017 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
4018 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
4020 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
4021 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4022 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
4023 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4024 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
4025 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4026 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4027 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
4028 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4029 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
4030 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
4031 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
4032 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
4048 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
4049 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
4050 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
4051 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
4052 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
4053 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
4054 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
4055 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
4056 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
4058 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
4059 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
4060 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
4062 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
4063 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
4064 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
4066 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
4067 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
4068 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
4070 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
4071 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
4072 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
4074 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
4075 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
4076 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
4078 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
4079 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
4080 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
4082 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
4083 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
4084 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
4086 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
4087 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
4088 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
4090 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
4091 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
4092 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
4094 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
4095 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
4096 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
4098 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
4099 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
4100 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
4102 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
4103 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
4104 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
4106 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
4107 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
4108 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
4110 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
4111 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
4112 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
4114 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
4115 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
4116 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
4118 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
4119 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
4120 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
4121 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
4122 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
4123 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
4124 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
4125 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
4126 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
4128 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
4129 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4130 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
4131 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4132 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
4133 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4134 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4135 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
4136 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4137 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
4138 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
4139 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
4140 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
4156 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
4157 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
4158 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
4159 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
4160 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
4161 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
4162 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
4163 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
4164 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
4166 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
4167 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
4168 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
4170 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
4171 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
4172 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
4174 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
4175 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
4176 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
4178 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
4179 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
4180 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
4182 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
4183 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
4184 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
4186 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
4187 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
4188 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
4190 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
4191 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
4192 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
4194 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
4195 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
4196 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
4198 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
4199 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
4200 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
4202 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
4203 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
4204 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
4206 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
4207 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
4208 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
4210 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
4211 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
4212 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
4214 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
4215 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
4216 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
4218 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
4219 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
4220 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
4222 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
4223 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
4224 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
4226 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
4227 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
4228 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
4229 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
4230 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
4231 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
4232 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
4233 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
4234 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
4236 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
4237 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4238 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
4239 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4240 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
4241 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4242 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4243 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
4244 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4245 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
4246 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
4247 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
4248 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
4264 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
4265 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
4266 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
4267 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
4268 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
4269 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
4270 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
4271 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
4272 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
4274 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
4275 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
4276 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
4278 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
4279 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
4280 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
4282 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
4283 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
4284 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
4286 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
4287 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
4288 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
4290 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
4291 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
4292 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
4294 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
4295 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
4296 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
4298 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
4299 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
4300 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
4302 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
4303 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
4304 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
4306 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
4307 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
4308 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
4310 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
4311 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
4312 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
4314 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
4315 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
4316 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
4318 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
4319 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
4320 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
4322 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
4323 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
4324 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
4326 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
4327 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
4328 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
4330 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
4331 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
4332 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
4334 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
4335 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
4336 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
4337 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
4338 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
4339 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
4340 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
4341 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
4342 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
4344 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
4345 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4346 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
4347 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4348 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
4349 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4350 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4351 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
4352 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4353 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
4354 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
4355 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
4356 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
4372 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
4373 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
4374 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
4375 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
4376 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
4377 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
4378 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
4379 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
4380 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
4382 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
4383 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
4384 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
4386 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
4387 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
4388 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
4390 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
4391 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
4392 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
4394 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
4395 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
4396 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
4398 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
4399 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
4400 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
4402 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
4403 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
4404 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
4406 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
4407 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
4408 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
4410 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
4411 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
4412 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
4414 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
4415 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
4416 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
4418 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
4419 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
4420 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
4422 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
4423 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
4424 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
4426 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
4427 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
4428 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
4430 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
4431 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
4432 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
4434 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
4435 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
4436 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
4438 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
4439 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
4440 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
4442 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
4443 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
4444 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
4445 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
4446 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
4447 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
4448 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
4449 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
4450 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
4452 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
4453 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4454 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
4455 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4456 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
4457 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4458 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4459 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
4460 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4461 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
4462 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
4463 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
4464 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
4480 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
4481 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
4482 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
4483 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
4484 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
4485 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
4486 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
4487 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
4488 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
4490 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
4491 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
4492 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
4494 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
4495 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
4496 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
4498 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
4499 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
4500 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
4502 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
4503 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
4504 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
4506 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
4507 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
4508 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
4510 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
4511 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
4512 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
4514 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
4515 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
4516 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
4518 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
4519 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
4520 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
4522 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
4523 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
4524 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
4526 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
4527 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
4528 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
4530 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
4531 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
4532 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
4534 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
4535 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
4536 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
4538 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
4539 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
4540 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
4542 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
4543 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
4544 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
4546 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
4547 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
4548 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
4550 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
4551 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
4552 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
4553 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
4554 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
4555 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
4556 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
4557 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
4558 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
4560 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
4561 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4562 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
4563 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4564 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
4565 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4566 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4567 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
4568 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4569 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
4570 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
4571 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
4572 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
4588 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
4589 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
4590 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
4591 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
4592 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
4593 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
4594 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
4595 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
4596 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
4598 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
4599 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
4600 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
4602 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
4603 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
4604 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
4606 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
4607 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
4608 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
4610 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
4611 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
4612 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
4614 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
4615 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
4616 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
4618 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
4619 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
4620 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
4622 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
4623 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
4624 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
4626 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
4627 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
4628 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
4630 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
4631 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
4632 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
4634 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
4635 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
4636 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
4638 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
4639 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
4640 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
4642 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
4643 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
4644 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
4646 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
4647 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
4648 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
4650 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
4651 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
4652 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
4654 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
4655 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
4656 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
4658 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
4659 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
4660 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
4661 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
4662 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
4663 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
4664 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
4665 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
4666 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
4668 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
4669 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4670 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
4671 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4672 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
4673 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4674 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4675 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
4676 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4677 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
4678 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
4679 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
4680 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
4696 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
4697 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
4698 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
4699 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
4700 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
4701 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
4702 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
4703 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
4704 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
4706 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
4707 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
4708 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
4710 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
4711 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
4712 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
4714 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
4715 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
4716 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
4718 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
4719 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
4720 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
4722 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
4723 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
4724 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
4726 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
4727 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
4728 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
4730 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
4731 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
4732 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
4734 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
4735 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
4736 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
4738 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
4739 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
4740 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
4742 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
4743 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
4744 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
4746 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
4747 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
4748 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
4750 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
4751 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
4752 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
4754 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
4755 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
4756 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
4758 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
4759 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
4760 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
4762 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
4763 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
4764 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
4766 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
4767 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
4768 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
4769 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
4770 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
4771 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
4772 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
4773 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
4774 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
4776 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
4777 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4778 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
4779 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4780 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
4781 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4782 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4783 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
4784 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4785 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
4786 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
4787 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
4788 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
4804 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
4805 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
4806 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
4807 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
4808 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
4809 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
4810 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
4811 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
4812 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
4814 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
4815 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
4816 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
4818 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
4819 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
4820 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
4822 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
4823 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
4824 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
4826 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
4827 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
4828 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
4830 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
4831 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
4832 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
4834 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
4835 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
4836 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
4838 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
4839 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
4840 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
4842 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
4843 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
4844 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
4846 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
4847 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
4848 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
4850 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
4851 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
4852 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
4854 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
4855 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
4856 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
4858 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
4859 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
4860 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
4862 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
4863 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
4864 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
4866 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
4867 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
4868 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
4870 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
4871 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
4872 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
4874 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
4875 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
4876 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
4877 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
4878 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
4879 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
4880 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
4881 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
4882 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
4884 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
4885 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4886 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
4887 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4888 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
4889 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4890 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4891 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
4892 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4893 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
4894 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
4895 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
4896 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
4912 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
4913 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
4914 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
4915 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
4916 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
4917 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
4918 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
4919 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
4920 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
4922 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
4923 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
4924 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
4926 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
4927 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
4928 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
4930 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
4931 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
4932 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
4934 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
4935 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
4936 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
4938 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
4939 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
4940 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
4942 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
4943 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
4944 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
4946 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
4947 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
4948 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
4950 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
4951 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
4952 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
4954 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
4955 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
4956 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
4958 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
4959 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
4960 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
4962 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
4963 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
4964 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
4966 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
4967 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
4968 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
4970 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
4971 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
4972 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
4974 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
4975 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
4976 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
4978 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
4979 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
4980 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
4982 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
4983 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
4984 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
4985 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
4986 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
4987 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
4988 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
4989 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
4990 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
4992 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
4993 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4994 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
4995 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4996 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
4997 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
4998 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
4999 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
5000 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5001 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
5002 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
5003 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
5004 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
5020 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
5021 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
5022 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
5023 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
5024 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
5025 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
5026 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
5027 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
5028 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
5030 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
5031 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
5032 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
5034 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
5035 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
5036 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
5038 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
5039 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
5040 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
5042 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
5043 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
5044 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
5046 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
5047 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
5048 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
5050 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
5051 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
5052 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
5054 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
5055 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
5056 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
5058 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
5059 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
5060 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
5062 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
5063 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
5064 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
5066 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
5067 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
5068 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
5070 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
5071 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
5072 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
5074 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
5075 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
5076 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
5078 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
5079 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
5080 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
5082 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
5083 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
5084 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
5086 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
5087 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
5088 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
5090 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
5091 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
5092 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
5093 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
5094 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
5095 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
5096 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
5097 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
5098 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
5100 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
5101 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5102 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
5103 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5104 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
5105 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5106 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5107 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
5108 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5109 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
5110 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
5111 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
5112 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
5128 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
5129 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
5130 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
5131 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
5132 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
5133 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
5134 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
5135 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
5136 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
5138 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
5139 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
5140 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
5142 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
5143 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
5144 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
5146 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
5147 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
5148 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
5150 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
5151 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
5152 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
5154 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
5155 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
5156 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
5158 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
5159 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
5160 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
5162 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
5163 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
5164 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
5166 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
5167 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
5168 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
5170 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
5171 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
5172 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
5174 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
5175 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
5176 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
5178 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
5179 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
5180 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
5182 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
5183 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
5184 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
5186 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
5187 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
5188 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
5190 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
5191 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
5192 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
5194 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
5195 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
5196 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
5198 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
5199 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
5200 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
5201 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
5202 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
5203 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
5204 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
5205 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
5206 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
5208 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
5209 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5210 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
5211 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5212 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
5213 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5214 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5215 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
5216 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5217 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
5218 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
5219 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
5220 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
5236 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
5237 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
5238 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
5239 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
5240 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
5241 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
5242 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
5243 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
5244 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
5246 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
5247 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
5248 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
5250 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
5251 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
5252 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
5254 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
5255 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
5256 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
5258 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
5259 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
5260 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
5262 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
5263 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
5264 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
5266 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
5267 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
5268 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
5270 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
5271 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
5272 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
5274 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
5275 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
5276 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
5278 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
5279 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
5280 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
5282 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
5283 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
5284 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
5286 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
5287 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
5288 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
5290 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
5291 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
5292 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
5294 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
5295 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
5296 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
5298 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
5299 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
5300 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
5302 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
5303 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
5304 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
5306 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
5307 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
5308 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
5309 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
5310 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
5311 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
5312 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
5313 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
5314 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
5316 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
5317 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5318 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
5319 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5320 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
5321 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5322 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5323 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
5324 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5325 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
5326 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
5327 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
5328 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
5344 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
5345 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
5346 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
5347 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
5348 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
5349 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
5350 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
5351 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
5352 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
5354 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
5355 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
5356 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
5358 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
5359 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
5360 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
5362 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
5363 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
5364 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
5366 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
5367 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
5368 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
5370 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
5371 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
5372 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
5374 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
5375 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
5376 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
5378 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
5379 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
5380 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
5382 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
5383 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
5384 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
5386 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
5387 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
5388 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
5390 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
5391 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
5392 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
5394 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
5395 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
5396 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
5398 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
5399 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
5400 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
5402 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
5403 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
5404 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
5406 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
5407 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
5408 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
5410 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
5411 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
5412 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
5414 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
5415 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
5416 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
5417 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
5418 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
5419 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
5420 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
5421 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
5422 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
5424 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
5425 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5426 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
5427 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5428 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
5429 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5430 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5431 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
5432 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5433 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
5434 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
5435 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
5436 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
5452 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
5453 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
5454 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
5455 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
5456 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
5457 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
5458 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
5459 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
5460 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
5462 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
5463 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
5464 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
5466 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
5467 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
5468 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
5470 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
5471 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
5472 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
5474 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
5475 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
5476 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
5478 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
5479 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
5480 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
5482 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
5483 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
5484 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
5486 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
5487 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
5488 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
5490 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
5491 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
5492 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
5494 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
5495 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
5496 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
5498 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
5499 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
5500 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
5502 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
5503 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
5504 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
5506 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
5507 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
5508 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
5510 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
5511 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
5512 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
5514 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
5515 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
5516 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
5518 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
5519 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
5520 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
5522 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
5523 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
5524 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
5525 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
5526 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
5527 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
5528 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
5529 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
5530 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
5532 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
5533 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5534 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
5535 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5536 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
5537 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5538 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5539 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
5540 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5541 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
5542 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
5543 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
5544 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
5560 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
5561 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
5562 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
5563 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
5564 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
5565 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
5566 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
5567 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
5568 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
5570 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
5571 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
5572 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
5574 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
5575 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
5576 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
5578 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
5579 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
5580 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
5582 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
5583 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
5584 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
5586 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
5587 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
5588 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
5590 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
5591 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
5592 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
5594 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
5595 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
5596 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
5598 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
5599 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
5600 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
5602 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
5603 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
5604 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
5606 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
5607 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
5608 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
5610 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
5611 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
5612 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
5614 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
5615 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
5616 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
5618 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
5619 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
5620 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
5622 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
5623 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
5624 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
5626 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
5627 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
5628 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
5630 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
5631 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
5632 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
5633 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
5634 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
5635 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
5636 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
5637 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
5638 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
5640 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
5641 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5642 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
5643 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5644 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
5645 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5646 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5647 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
5648 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5649 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
5650 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
5651 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
5652 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
5668 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
5669 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
5670 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
5671 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
5672 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
5673 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
5674 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
5675 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
5676 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
5678 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
5679 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
5680 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
5682 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
5683 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
5684 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
5686 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
5687 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
5688 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
5690 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
5691 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
5692 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
5694 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
5695 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
5696 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
5698 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
5699 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
5700 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
5702 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
5703 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
5704 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
5706 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
5707 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
5708 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
5710 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
5711 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
5712 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
5714 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
5715 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
5716 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
5718 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
5719 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
5720 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
5722 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
5723 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
5724 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
5726 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
5727 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
5728 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
5730 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
5731 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
5732 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
5734 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
5735 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
5736 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
5738 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
5739 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
5740 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
5741 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
5742 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
5743 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
5744 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
5745 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
5746 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
5748 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
5749 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5750 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
5751 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5752 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
5753 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5754 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5755 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
5756 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5757 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
5758 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
5759 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
5760 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
5776 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
5777 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
5778 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
5779 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
5780 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
5781 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
5782 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
5783 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
5784 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
5786 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
5787 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
5788 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
5790 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
5791 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
5792 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
5794 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
5795 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
5796 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
5798 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
5799 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
5800 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
5802 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
5803 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
5804 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
5806 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
5807 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
5808 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
5810 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
5811 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
5812 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
5814 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
5815 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
5816 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
5818 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
5819 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
5820 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
5822 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
5823 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
5824 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
5826 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
5827 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
5828 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
5830 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
5831 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
5832 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
5834 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
5835 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
5836 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
5838 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
5839 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
5840 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
5842 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
5843 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
5844 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
5846 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
5847 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
5848 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
5849 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
5850 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
5851 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
5852 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
5853 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
5854 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
5856 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
5857 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5858 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
5859 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5860 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
5861 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5862 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5863 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
5864 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5865 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
5866 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
5867 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
5868 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
5884 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
5885 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
5886 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
5887 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
5888 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
5889 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
5890 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
5891 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
5892 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
5894 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
5895 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
5896 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
5898 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
5899 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
5900 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
5902 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
5903 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
5904 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
5906 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
5907 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
5908 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
5910 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
5911 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
5912 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
5914 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
5915 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
5916 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
5918 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
5919 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
5920 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
5922 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
5923 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
5924 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
5926 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
5927 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
5928 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
5930 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
5931 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
5932 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
5934 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
5935 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
5936 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
5938 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
5939 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
5940 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
5942 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
5943 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
5944 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
5946 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
5947 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
5948 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
5950 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
5951 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
5952 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
5954 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
5955 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
5956 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
5957 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
5958 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
5959 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
5960 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
5961 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
5962 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
5964 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
5965 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5966 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
5967 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5968 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
5969 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
5970 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5971 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
5972 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
5973 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
5974 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
5975 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
5976 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
5992 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
5993 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
5994 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
5995 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
5996 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
5997 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
5998 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
5999 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
6000 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
6002 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
6003 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
6004 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
6006 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
6007 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
6008 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
6010 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
6011 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
6012 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
6014 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
6015 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
6016 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
6018 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
6019 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
6020 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
6022 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
6023 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
6024 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
6026 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
6027 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
6028 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
6030 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
6031 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
6032 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
6034 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
6035 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
6036 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
6038 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
6039 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
6040 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
6042 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
6043 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
6044 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
6046 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
6047 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
6048 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
6050 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
6051 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
6052 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
6054 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
6055 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
6056 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
6058 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
6059 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
6060 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
6062 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
6063 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
6064 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
6065 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
6066 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
6067 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
6068 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
6069 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
6070 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
6072 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
6073 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6074 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
6075 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6076 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
6077 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6078 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6079 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
6080 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6081 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
6082 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
6083 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
6084 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
6100 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
6101 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
6102 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
6103 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
6104 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
6105 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
6106 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
6107 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
6108 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
6110 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
6111 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
6112 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
6114 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
6115 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
6116 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
6118 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
6119 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
6120 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
6122 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
6123 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
6124 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
6126 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
6127 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
6128 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
6130 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
6131 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
6132 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
6134 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
6135 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
6136 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
6138 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
6139 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
6140 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
6142 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
6143 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
6144 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
6146 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
6147 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
6148 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
6150 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
6151 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
6152 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
6154 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
6155 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
6156 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
6158 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
6159 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
6160 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
6162 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
6163 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
6164 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
6166 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
6167 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
6168 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
6170 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
6171 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
6172 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
6173 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
6174 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
6175 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
6176 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
6177 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
6178 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
6180 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
6181 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6182 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
6183 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6184 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
6185 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6186 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6187 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
6188 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6189 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
6190 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
6191 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
6192 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
6208 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
6209 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
6210 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
6211 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
6212 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
6213 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
6214 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
6215 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
6216 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
6218 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
6219 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
6220 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
6222 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
6223 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
6224 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
6226 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
6227 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
6228 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
6230 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
6231 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
6232 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
6234 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
6235 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
6236 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
6238 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
6239 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
6240 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
6242 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
6243 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
6244 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
6246 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
6247 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
6248 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
6250 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
6251 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
6252 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
6254 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
6255 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
6256 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
6258 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
6259 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
6260 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
6262 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
6263 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
6264 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
6266 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
6267 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
6268 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
6270 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
6271 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
6272 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
6274 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
6275 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
6276 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
6278 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
6279 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
6280 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
6281 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
6282 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
6283 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
6284 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
6285 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
6286 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
6288 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
6289 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6290 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
6291 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6292 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
6293 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6294 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6295 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
6296 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6297 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
6298 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
6299 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
6300 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
6316 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
6317 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
6318 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
6319 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
6320 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
6321 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
6322 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
6323 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
6324 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
6326 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
6327 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
6328 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
6330 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
6331 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
6332 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
6334 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
6335 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
6336 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
6338 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
6339 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
6340 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
6342 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
6343 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
6344 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
6346 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
6347 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
6348 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
6350 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
6351 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
6352 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
6354 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
6355 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
6356 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
6358 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
6359 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
6360 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
6362 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
6363 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
6364 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
6366 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
6367 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
6368 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
6370 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
6371 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
6372 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
6374 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
6375 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
6376 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
6378 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
6379 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
6380 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
6382 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
6383 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
6384 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
6386 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
6387 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
6388 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
6389 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
6390 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
6391 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
6392 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
6393 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
6394 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
6396 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
6397 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6398 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
6399 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6400 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
6401 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6402 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6403 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
6404 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6405 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
6406 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
6407 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
6408 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
6424 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
6425 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
6426 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
6427 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
6428 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
6429 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
6430 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
6431 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
6432 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
6434 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
6435 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
6436 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
6438 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
6439 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
6440 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
6442 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
6443 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
6444 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
6446 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
6447 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
6448 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
6450 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
6451 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
6452 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
6454 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
6455 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
6456 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
6458 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
6459 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
6460 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
6462 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
6463 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
6464 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
6466 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
6467 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
6468 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
6470 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
6471 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
6472 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
6474 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
6475 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
6476 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
6478 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
6479 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
6480 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
6482 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
6483 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
6484 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
6486 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
6487 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
6488 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
6490 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
6491 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
6492 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
6494 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
6495 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
6496 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
6497 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
6498 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
6499 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
6500 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
6501 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
6502 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
6504 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
6505 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6506 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
6507 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6508 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
6509 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6510 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6511 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
6512 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6513 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
6514 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
6515 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
6516 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
6532 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
6533 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
6534 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
6535 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
6536 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
6537 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
6538 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
6539 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
6540 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
6542 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
6543 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
6544 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
6546 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
6547 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
6548 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
6550 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
6551 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
6552 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
6554 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
6555 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
6556 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
6558 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
6559 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
6560 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
6562 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
6563 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
6564 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
6566 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
6567 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
6568 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
6570 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
6571 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
6572 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
6574 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
6575 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
6576 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
6578 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
6579 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
6580 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
6582 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
6583 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
6584 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
6586 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
6587 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
6588 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
6590 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
6591 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
6592 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
6594 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
6595 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
6596 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
6598 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
6599 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
6600 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
6602 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
6603 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
6604 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
6605 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
6606 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
6607 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
6608 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
6609 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
6610 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
6612 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
6613 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6614 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
6615 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6616 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
6617 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6618 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6619 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
6620 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6621 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
6622 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
6623 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
6624 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
6640 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
6641 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
6642 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
6643 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
6644 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
6645 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
6646 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
6647 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
6648 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
6650 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
6651 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
6652 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
6654 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
6655 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
6656 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
6658 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
6659 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
6660 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
6662 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
6663 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
6664 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
6666 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
6667 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
6668 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
6670 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
6671 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
6672 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
6674 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
6675 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
6676 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
6678 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
6679 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
6680 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
6682 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
6683 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
6684 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
6686 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
6687 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
6688 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
6690 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
6691 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
6692 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
6694 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
6695 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
6696 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
6698 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
6699 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
6700 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
6702 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
6703 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
6704 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
6706 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
6707 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
6708 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
6710 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
6711 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
6712 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
6713 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
6714 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
6715 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
6716 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
6717 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
6718 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
6720 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
6721 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6722 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
6723 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6724 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
6725 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6726 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6727 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
6728 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6729 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
6730 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
6731 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
6732 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
6748 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
6749 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
6750 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
6751 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
6752 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
6753 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
6754 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
6755 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
6756 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
6758 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
6759 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
6760 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
6762 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
6763 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
6764 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
6766 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
6767 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
6768 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
6770 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
6771 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
6772 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
6774 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
6775 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
6776 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
6778 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
6779 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
6780 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
6782 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
6783 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
6784 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
6786 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
6787 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
6788 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
6790 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
6791 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
6792 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
6794 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
6795 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
6796 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
6798 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
6799 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
6800 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
6802 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
6803 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
6804 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
6806 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
6807 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
6808 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
6810 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
6811 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
6812 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
6814 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
6815 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
6816 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
6818 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
6819 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
6820 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
6821 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
6822 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
6823 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
6824 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
6825 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
6826 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
6828 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
6829 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6830 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
6831 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6832 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
6833 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6834 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6835 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
6836 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6837 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
6838 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
6839 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
6840 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
6856 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
6857 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
6858 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
6859 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
6860 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
6861 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
6862 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
6863 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
6864 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
6866 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
6867 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
6868 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
6870 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
6871 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
6872 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
6874 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
6875 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
6876 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
6878 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
6879 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
6880 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
6882 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
6883 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
6884 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
6886 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
6887 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
6888 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
6890 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
6891 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
6892 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
6894 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
6895 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
6896 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
6898 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
6899 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
6900 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
6902 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
6903 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
6904 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
6906 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
6907 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
6908 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
6910 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
6911 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
6912 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
6914 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
6915 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
6916 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
6918 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
6919 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
6920 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
6922 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
6923 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
6924 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
6926 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
6927 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
6928 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
6929 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
6930 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
6931 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
6932 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
6933 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
6934 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
6936 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
6937 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6938 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
6939 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6940 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
6941 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
6942 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6943 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
6944 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
6945 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
6946 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
6947 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
6948 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
6964 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
6965 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
6966 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
6967 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
6968 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
6969 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
6970 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
6971 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
6972 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
6974 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
6975 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
6976 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
6978 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
6979 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
6980 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
6982 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
6983 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
6984 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
6986 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
6987 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
6988 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
6990 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
6991 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
6992 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
6994 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
6995 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
6996 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
6998 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
6999 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
7000 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
7002 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
7003 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
7004 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
7006 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
7007 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
7008 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
7010 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
7011 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
7012 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
7014 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
7015 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
7016 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
7018 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
7019 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
7020 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
7022 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
7023 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
7024 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
7026 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
7027 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
7028 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
7030 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
7031 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
7032 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
7034 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
7035 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
7036 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
7037 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
7038 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
7039 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
7040 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
7041 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
7042 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
7044 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
7045 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7046 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
7047 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7048 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
7049 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7050 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7051 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
7052 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7053 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
7054 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
7055 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
7056 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
7072 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
7073 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
7074 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
7075 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
7076 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
7077 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
7078 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
7079 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
7080 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
7082 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
7083 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
7084 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
7086 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
7087 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
7088 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
7090 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
7091 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
7092 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
7094 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
7095 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
7096 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
7098 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
7099 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
7100 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
7102 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
7103 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
7104 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
7106 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
7107 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
7108 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
7110 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
7111 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
7112 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
7114 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
7115 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
7116 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
7118 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
7119 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
7120 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
7122 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
7123 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
7124 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
7126 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
7127 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
7128 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
7130 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
7131 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
7132 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
7134 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
7135 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
7136 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
7138 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
7139 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
7140 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
7142 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
7143 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
7144 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
7145 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
7146 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
7147 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
7148 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
7149 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
7150 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
7152 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
7153 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7154 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
7155 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7156 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
7157 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7158 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7159 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
7160 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7161 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
7162 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
7163 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
7164 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
7180 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
7181 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
7182 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
7183 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
7184 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
7185 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
7186 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
7187 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
7188 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
7190 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
7191 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
7192 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
7194 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
7195 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
7196 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
7198 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
7199 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
7200 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
7202 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
7203 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
7204 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
7206 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
7207 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
7208 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
7210 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
7211 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
7212 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
7214 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
7215 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
7216 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
7218 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
7219 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
7220 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
7222 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
7223 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
7224 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
7226 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
7227 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
7228 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
7230 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
7231 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
7232 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
7234 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
7235 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
7236 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
7238 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
7239 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
7240 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
7242 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
7243 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
7244 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
7246 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
7247 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
7248 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
7250 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
7251 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
7252 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
7253 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
7254 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
7255 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
7256 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
7257 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
7258 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
7260 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
7261 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7262 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
7263 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7264 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
7265 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7266 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7267 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
7268 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7269 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
7270 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
7271 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
7272 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
7288 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
7289 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
7290 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
7291 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
7292 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
7293 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
7294 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
7295 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
7296 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
7298 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
7299 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
7300 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
7302 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
7303 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
7304 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
7306 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
7307 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
7308 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
7310 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
7311 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
7312 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
7314 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
7315 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
7316 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
7318 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
7319 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
7320 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
7322 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
7323 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
7324 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
7326 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
7327 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
7328 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
7330 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
7331 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
7332 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
7334 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
7335 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
7336 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
7338 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
7339 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
7340 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
7342 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
7343 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
7344 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
7346 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
7347 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
7348 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
7350 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
7351 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
7352 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
7354 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
7355 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
7356 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
7358 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
7359 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
7360 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
7361 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
7362 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
7363 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
7364 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
7365 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
7366 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
7368 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
7369 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7370 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
7371 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7372 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
7373 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7374 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7375 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
7376 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7377 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
7378 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
7379 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
7380 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
7396 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
7397 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
7398 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
7399 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
7400 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
7401 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
7402 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
7403 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
7404 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
7406 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
7407 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
7408 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
7410 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
7411 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
7412 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
7414 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
7415 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
7416 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
7418 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
7419 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
7420 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
7422 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
7423 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
7424 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
7426 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
7427 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
7428 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
7430 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
7431 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
7432 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
7434 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
7435 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
7436 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
7438 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
7439 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
7440 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
7442 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
7443 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
7444 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
7446 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
7447 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
7448 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
7450 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
7451 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
7452 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
7454 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
7455 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
7456 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
7458 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
7459 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
7460 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
7462 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
7463 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
7464 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
7466 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
7467 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
7468 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
7469 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
7470 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
7471 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
7472 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
7473 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
7474 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
7476 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
7477 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7478 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
7479 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7480 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
7481 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7482 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7483 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
7484 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7485 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
7486 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
7487 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
7488 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
7504 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
7505 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
7506 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
7507 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
7508 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
7509 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
7510 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
7511 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
7512 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
7514 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
7515 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
7516 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
7518 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
7519 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
7520 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
7522 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
7523 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
7524 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
7526 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
7527 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
7528 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
7530 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
7531 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
7532 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
7534 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
7535 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
7536 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
7538 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
7539 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
7540 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
7542 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
7543 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
7544 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
7546 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
7547 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
7548 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
7550 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
7551 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
7552 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
7554 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
7555 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
7556 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
7558 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
7559 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
7560 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
7562 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
7563 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
7564 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
7566 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
7567 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
7568 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
7570 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
7571 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
7572 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
7574 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
7575 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
7576 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
7577 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
7578 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
7579 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
7580 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
7581 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
7582 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
7584 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
7585 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7586 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
7587 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7588 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
7589 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7590 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7591 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
7592 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7593 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
7594 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
7595 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
7596 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
7612 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
7613 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
7614 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
7615 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
7616 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
7617 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
7618 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
7619 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
7620 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
7622 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
7623 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
7624 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
7626 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
7627 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
7628 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
7630 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
7631 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
7632 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
7634 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
7635 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
7636 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
7638 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
7639 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
7640 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
7642 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
7643 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
7644 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
7646 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
7647 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
7648 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
7650 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
7651 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
7652 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
7654 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
7655 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
7656 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
7658 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
7659 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
7660 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
7662 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
7663 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
7664 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
7666 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
7667 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
7668 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
7670 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
7671 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
7672 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
7674 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
7675 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
7676 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
7678 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
7679 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
7680 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
7682 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
7683 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
7684 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
7685 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
7686 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
7687 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
7688 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
7689 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
7690 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
7692 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
7693 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7694 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
7695 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7696 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
7697 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7698 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7699 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
7700 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7701 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
7702 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
7703 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
7704 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
7720 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
7721 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
7722 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
7723 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
7724 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
7725 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
7726 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
7727 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
7728 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
7730 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
7731 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
7732 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
7734 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
7735 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
7736 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
7738 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
7739 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
7740 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
7742 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
7743 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
7744 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
7746 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
7747 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
7748 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
7750 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
7751 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
7752 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
7754 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
7755 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
7756 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
7758 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
7759 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
7760 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
7762 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
7763 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
7764 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
7766 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
7767 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
7768 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
7770 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
7771 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
7772 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
7774 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
7775 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
7776 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
7778 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
7779 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
7780 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
7782 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
7783 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
7784 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
7786 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
7787 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
7788 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
7790 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
7791 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
7792 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
7793 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
7794 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
7795 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
7796 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
7797 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
7798 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
7800 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
7801 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7802 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
7803 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7804 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
7805 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7806 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7807 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
7808 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7809 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
7810 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
7811 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
7812 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
7828 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
7829 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
7830 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
7831 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
7832 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
7833 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
7834 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
7835 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
7836 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
7838 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
7839 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
7840 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
7842 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
7843 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
7844 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
7846 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
7847 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
7848 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
7850 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
7851 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
7852 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
7854 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
7855 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
7856 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
7858 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
7859 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
7860 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
7862 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
7863 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
7864 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
7866 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
7867 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
7868 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
7870 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
7871 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
7872 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
7874 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
7875 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
7876 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
7878 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
7879 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
7880 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
7882 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
7883 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
7884 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
7886 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
7887 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
7888 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
7890 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
7891 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
7892 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
7894 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
7895 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
7896 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
7898 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
7899 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
7900 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
7901 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
7902 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
7903 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
7904 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
7905 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
7906 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
7908 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
7909 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7910 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
7911 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7912 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
7913 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
7914 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7915 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
7916 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
7917 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
7918 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
7919 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
7920 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
7936 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
7937 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
7938 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
7939 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
7940 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
7941 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
7942 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
7943 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
7944 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
7946 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
7947 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
7948 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
7950 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
7951 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
7952 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
7954 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
7955 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
7956 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
7958 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
7959 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
7960 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
7962 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
7963 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
7964 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
7966 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
7967 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
7968 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
7970 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
7971 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
7972 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
7974 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
7975 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
7976 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
7978 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
7979 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
7980 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
7982 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
7983 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
7984 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
7986 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
7987 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
7988 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
7990 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
7991 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
7992 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
7994 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
7995 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
7996 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
7998 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
7999 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
8000 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
8002 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
8003 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
8004 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
8006 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
8007 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
8008 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
8009 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
8010 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
8011 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
8012 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
8013 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
8014 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
8016 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
8017 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8018 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
8019 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8020 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
8021 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8022 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8023 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
8024 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8025 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
8026 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
8027 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
8028 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
8044 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
8045 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
8046 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
8047 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
8048 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
8049 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
8050 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
8051 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
8052 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
8054 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
8055 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
8056 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
8058 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
8059 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
8060 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
8062 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
8063 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
8064 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
8066 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
8067 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
8068 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
8070 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
8071 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
8072 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
8074 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
8075 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
8076 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
8078 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
8079 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
8080 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
8082 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
8083 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
8084 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
8086 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
8087 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
8088 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
8090 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
8091 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
8092 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
8094 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
8095 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
8096 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
8098 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
8099 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
8100 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
8102 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
8103 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
8104 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
8106 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
8107 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
8108 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
8110 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
8111 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
8112 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
8114 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
8115 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
8116 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
8117 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
8118 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
8119 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
8120 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
8121 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
8122 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
8124 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
8125 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8126 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
8127 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8128 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
8129 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8130 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8131 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
8132 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8133 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
8134 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
8135 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
8136 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
8152 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
8153 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
8154 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
8155 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
8156 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
8157 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
8158 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
8159 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
8160 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
8162 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
8163 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
8164 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
8166 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
8167 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
8168 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
8170 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
8171 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
8172 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
8174 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
8175 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
8176 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
8178 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
8179 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
8180 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
8182 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
8183 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
8184 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
8186 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
8187 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
8188 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
8190 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
8191 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
8192 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
8194 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
8195 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
8196 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
8198 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
8199 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
8200 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
8202 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
8203 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
8204 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
8206 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
8207 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
8208 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
8210 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
8211 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
8212 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
8214 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
8215 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
8216 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
8218 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
8219 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
8220 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
8222 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
8223 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
8224 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
8225 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
8226 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
8227 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
8228 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
8229 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
8230 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
8232 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
8233 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8234 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
8235 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8236 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
8237 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8238 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8239 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
8240 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8241 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
8242 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
8243 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
8244 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
8260 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
8261 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
8262 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
8263 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
8264 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
8265 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
8266 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
8267 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
8268 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
8270 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
8271 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
8272 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
8274 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
8275 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
8276 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
8278 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
8279 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
8280 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
8282 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
8283 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
8284 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
8286 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
8287 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
8288 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
8290 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
8291 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
8292 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
8294 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
8295 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
8296 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
8298 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
8299 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
8300 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
8302 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
8303 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
8304 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
8306 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
8307 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
8308 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
8310 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
8311 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
8312 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
8314 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
8315 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
8316 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
8318 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
8319 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
8320 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
8322 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
8323 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
8324 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
8326 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
8327 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
8328 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
8330 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
8331 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
8332 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
8333 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
8334 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
8335 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
8336 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
8337 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
8338 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
8340 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
8341 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8342 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
8343 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8344 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
8345 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8346 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8347 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
8348 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8349 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
8350 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
8351 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
8352 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
8368 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
8369 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
8370 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
8371 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
8372 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
8373 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
8374 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
8375 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
8376 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
8378 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
8379 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
8380 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
8382 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
8383 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
8384 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
8386 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
8387 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
8388 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
8390 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
8391 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
8392 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
8394 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
8395 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
8396 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
8398 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
8399 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
8400 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
8402 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
8403 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
8404 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
8406 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
8407 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
8408 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
8410 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
8411 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
8412 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
8414 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
8415 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
8416 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
8418 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
8419 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
8420 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
8422 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
8423 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
8424 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
8426 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
8427 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
8428 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
8430 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
8431 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
8432 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
8434 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
8435 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
8436 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
8438 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
8439 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
8440 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
8441 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
8442 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
8443 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
8444 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
8445 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
8446 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
8448 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
8449 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8450 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
8451 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8452 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
8453 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8454 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8455 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
8456 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8457 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
8458 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
8459 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
8460 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
8476 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
8477 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
8478 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
8479 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
8480 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
8481 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
8482 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
8483 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
8484 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
8486 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
8487 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
8488 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
8490 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
8491 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
8492 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
8494 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
8495 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
8496 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
8498 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
8499 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
8500 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
8502 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
8503 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
8504 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
8506 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
8507 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
8508 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
8510 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
8511 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
8512 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
8514 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
8515 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
8516 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
8518 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
8519 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
8520 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
8522 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
8523 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
8524 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
8526 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
8527 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
8528 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
8530 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
8531 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
8532 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
8534 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
8535 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
8536 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
8538 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
8539 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
8540 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
8542 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
8543 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
8544 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
8546 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
8547 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
8548 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
8549 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
8550 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
8551 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
8552 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
8553 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
8554 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
8556 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
8557 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8558 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
8559 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8560 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
8561 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8562 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8563 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
8564 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8565 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
8566 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
8567 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
8568 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
8584 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
8585 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
8586 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
8587 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
8588 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
8589 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
8590 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
8591 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
8592 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
8594 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
8595 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
8596 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
8598 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
8599 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
8600 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
8602 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
8603 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
8604 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
8606 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
8607 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
8608 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
8610 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
8611 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
8612 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
8614 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
8615 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
8616 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
8618 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
8619 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
8620 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
8622 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
8623 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
8624 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
8626 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
8627 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
8628 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
8630 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
8631 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
8632 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
8634 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
8635 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
8636 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
8638 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
8639 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
8640 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
8642 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
8643 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
8644 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
8646 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
8647 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
8648 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
8650 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
8651 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
8652 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
8654 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
8655 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
8656 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
8657 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
8658 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
8659 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
8660 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
8661 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
8662 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
8664 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
8665 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8666 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
8667 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8668 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
8669 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8670 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8671 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
8672 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8673 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
8674 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
8675 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
8676 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
8692 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
8693 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
8694 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
8695 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
8696 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
8697 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
8698 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
8699 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
8700 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
8702 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
8703 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
8704 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
8706 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
8707 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
8708 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
8710 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
8711 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
8712 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
8714 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
8715 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
8716 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
8718 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
8719 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
8720 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
8722 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
8723 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
8724 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
8726 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
8727 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
8728 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
8730 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
8731 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
8732 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
8734 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
8735 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
8736 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
8738 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
8739 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
8740 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
8742 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
8743 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
8744 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
8746 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
8747 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
8748 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
8750 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
8751 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
8752 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
8754 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
8755 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
8756 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
8758 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
8759 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
8760 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
8762 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
8763 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
8764 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
8765 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
8766 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
8767 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
8768 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
8769 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
8770 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
8772 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
8773 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8774 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
8775 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8776 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
8777 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8778 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8779 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
8780 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8781 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
8782 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
8783 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
8784 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
8800 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
8801 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
8802 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
8803 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
8804 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
8805 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
8806 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
8807 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
8808 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
8810 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
8811 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
8812 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
8814 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
8815 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
8816 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
8818 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
8819 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
8820 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
8822 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
8823 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
8824 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
8826 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
8827 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
8828 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
8830 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
8831 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
8832 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
8834 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
8835 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
8836 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
8838 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
8839 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
8840 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
8842 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
8843 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
8844 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
8846 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
8847 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
8848 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
8850 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
8851 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
8852 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
8854 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
8855 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
8856 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
8858 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
8859 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
8860 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
8862 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
8863 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
8864 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
8866 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
8867 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
8868 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
8870 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
8871 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
8872 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
8873 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
8874 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
8875 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
8876 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
8877 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
8878 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
8880 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
8881 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8882 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
8883 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8884 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
8885 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8886 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8887 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
8888 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8889 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
8890 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
8891 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
8892 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
8908 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
8909 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
8910 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
8911 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
8912 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
8913 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
8914 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
8915 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
8916 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
8918 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
8919 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
8920 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
8922 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
8923 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
8924 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
8926 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
8927 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
8928 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
8930 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
8931 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
8932 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
8934 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
8935 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
8936 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
8938 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
8939 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
8940 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
8942 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
8943 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
8944 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
8946 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
8947 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
8948 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
8950 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
8951 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
8952 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
8954 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
8955 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
8956 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
8958 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
8959 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
8960 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
8962 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
8963 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
8964 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
8966 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
8967 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
8968 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
8970 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
8971 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
8972 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
8974 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
8975 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
8976 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
8978 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
8979 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
8980 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
8981 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
8982 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
8983 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
8984 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
8985 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
8986 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
8988 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
8989 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8990 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
8991 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8992 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
8993 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
8994 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8995 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
8996 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
8997 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
8998 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
8999 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
9000 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
9016 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
9017 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
9018 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
9019 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
9020 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
9021 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
9022 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
9023 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
9024 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
9026 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
9027 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
9028 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
9030 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
9031 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
9032 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
9034 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
9035 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
9036 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
9038 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
9039 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
9040 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
9042 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
9043 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
9044 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
9046 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
9047 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
9048 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
9050 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
9051 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
9052 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
9054 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
9055 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
9056 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
9058 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
9059 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
9060 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
9062 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
9063 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
9064 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
9066 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
9067 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
9068 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
9070 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
9071 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
9072 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
9074 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
9075 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
9076 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
9078 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
9079 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
9080 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
9082 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
9083 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
9084 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
9086 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
9087 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
9088 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
9089 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
9090 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
9091 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
9092 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
9093 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
9094 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
9096 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
9097 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
9098 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
9099 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
9100 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
9101 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
9102 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
9103 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
9104 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
9105 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
9106 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
9107 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
9108 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
9124 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
9125 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
9126 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
9127 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
9128 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
9129 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
9130 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
9131 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
9132 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
9134 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
9135 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
9136 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
9138 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
9139 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
9140 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
9142 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
9143 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
9144 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
9146 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
9147 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
9148 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
9150 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
9151 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
9152 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
9154 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
9155 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
9156 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
9158 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
9159 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
9160 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
9162 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
9163 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
9164 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
9166 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
9167 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
9168 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
9170 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
9171 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
9172 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
9174 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
9175 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
9176 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
9178 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
9179 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
9180 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
9182 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
9183 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
9184 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
9186 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
9187 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
9188 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
9190 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
9191 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
9192 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
9194 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
9195 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
9196 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
9197 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
9198 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
9199 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
9200 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
9201 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
9202 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
9204 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
9205 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
9206 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
9207 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
9208 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
9209 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
9210 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
9211 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
9212 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
9213 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
9214 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
9215 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
9216 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
9232 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
9233 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
9234 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
9235 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
9236 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
9237 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
9238 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
9239 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
9240 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
9242 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
9243 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
9244 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
9246 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
9247 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
9248 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
9250 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
9251 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
9252 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
9254 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
9255 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
9256 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
9258 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
9259 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
9260 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
9262 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
9263 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
9264 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
9266 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
9267 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
9268 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
9270 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
9271 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
9272 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
9274 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
9275 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
9276 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
9278 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
9279 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
9280 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
9282 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
9283 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
9284 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
9286 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
9287 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
9288 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
9290 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
9291 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
9292 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
9294 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
9295 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
9296 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
9298 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
9299 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
9300 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
9302 | lithium-ion-module | Lithium-Ion Module Model | ID | Model identifier | uint16 |  | TRUE | TRUE
9303 | lithium-ion-module | Lithium-Ion Module Model | L | Model length | uint16 |  | TRUE | TRUE
9304 | lithium-ion-module | Lithium-Ion Module Model | StrIdx | Index of the string containing the module. | uint16 |  | TRUE | TRUE
9305 | lithium-ion-module | Lithium-Ion Module Model | ModIdx | Index of the module within the string. | uint16 |  | TRUE | TRUE
9306 | lithium-ion-module | Lithium-Ion Module Model | NCell | Count of all cells in the module. | uint16 |  | TRUE | TRUE
9307 | lithium-ion-module | Lithium-Ion Module Model | SoC | Module state of charge, expressed as a percentage. | uint16 |  | FALSE | FALSE
9308 | lithium-ion-module | Lithium-Ion Module Model | DoD | Depth of discharge for the module. | uint16 |  | FALSE | FALSE
9309 | lithium-ion-module | Lithium-Ion Module Model | SoH | Module state of health, expressed as a percentage. | uint16 |  | FALSE | FALSE
9310 | lithium-ion-module | Lithium-Ion Module Model | NCyc | Count of cycles executed. | uint32 |  | FALSE | FALSE
9312 | lithium-ion-module | Lithium-Ion Module Model | V | Voltage of the module. | uint16 |  | TRUE | TRUE
9313 | lithium-ion-module | Lithium-Ion Module Model | CellVMax | Maximum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
9314 | lithium-ion-module | Lithium-Ion Module Model | CellVMaxCell | Cell with the maximum voltage. | uint16 |  | FALSE | FALSE
9315 | lithium-ion-module | Lithium-Ion Module Model | CellVMin | Minimum voltage for all cells in the module. | uint16 |  | TRUE | TRUE
9316 | lithium-ion-module | Lithium-Ion Module Model | CellVMinCell | Cell with the minimum voltage. | uint16 |  | FALSE | FALSE
9317 | lithium-ion-module | Lithium-Ion Module Model | CellVAvg | Average voltage for all cells in the module. | uint16 |  | TRUE | TRUE
9318 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMax | Maximum temperature for all cells in the module. | int16 |  | TRUE | TRUE
9319 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMaxCell | Cell with the maximum cell temperature. | uint16 |  | FALSE | FALSE
9320 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMin | Minimum temperature for all cells in the module. | int16 |  | TRUE | TRUE
9321 | lithium-ion-module | Lithium-Ion Module Model | CellTmpMinCell | Cell with the minimum cell temperature. | uint16 |  | FALSE | FALSE
9322 | lithium-ion-module | Lithium-Ion Module Model | CellTmpAvg | Average temperature for all cells in the module. | int16 |  | TRUE | TRUE
9323 | lithium-ion-module | Lithium-Ion Module Model | NCellBal | Number of cells currently being balanced in the module. | uint16 |  | FALSE | FALSE
9324 | lithium-ion-module | Lithium-Ion Module Model | SN | Serial number for the module. | string |  | FALSE | FALSE
9340 | lithium-ion-module | Lithium-Ion Module Model | SoC_SF | Scale factor for module state of charge. | sunssf |  | FALSE | FALSE
9341 | lithium-ion-module | Lithium-Ion Module Model | SoH_SF | Scale factor for module state of health. | sunssf |  | FALSE | FALSE
9342 | lithium-ion-module | Lithium-Ion Module Model | DoD_SF | Scale factor for module depth of discharge. | sunssf |  | FALSE | FALSE
9343 | lithium-ion-module | Lithium-Ion Module Model | V_SF | Scale factor for module voltage. | sunssf |  | TRUE | TRUE
9344 | lithium-ion-module | Lithium-Ion Module Model | CellV_SF | Scale factor for cell voltage. | sunssf |  | TRUE | TRUE
9345 | lithium-ion-module | Lithium-Ion Module Model | Tmp_SF | Scale factor for module temperature. | sunssf |  | TRUE | TRUE
9346 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.0 | TRUE | TRUE
9347 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.0 | TRUE | TRUE
9348 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.0 | FALSE | TRUE
9350 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.1 | TRUE | TRUE
9351 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.1 | TRUE | TRUE
9352 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.1 | FALSE | TRUE
9354 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.2 | TRUE | TRUE
9355 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.2 | TRUE | TRUE
9356 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.2 | FALSE | TRUE
9358 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.3 | TRUE | TRUE
9359 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.3 | TRUE | TRUE
9360 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.3 | FALSE | TRUE
9362 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.4 | TRUE | TRUE
9363 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.4 | TRUE | TRUE
9364 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.4 | FALSE | TRUE
9366 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.5 | TRUE | TRUE
9367 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.5 | TRUE | TRUE
9368 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.5 | FALSE | TRUE
9370 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.6 | TRUE | TRUE
9371 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.6 | TRUE | TRUE
9372 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.6 | FALSE | TRUE
9374 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.7 | TRUE | TRUE
9375 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.7 | TRUE | TRUE
9376 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.7 | FALSE | TRUE
9378 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.8 | TRUE | TRUE
9379 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.8 | TRUE | TRUE
9380 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.8 | FALSE | TRUE
9382 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.9 | TRUE | TRUE
9383 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.9 | TRUE | TRUE
9384 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.9 | FALSE | TRUE
9386 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.10 | TRUE | TRUE
9387 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.10 | TRUE | TRUE
9388 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.10 | FALSE | TRUE
9390 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.11 | TRUE | TRUE
9391 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.11 | TRUE | TRUE
9392 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.11 | FALSE | TRUE
9394 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.12 | TRUE | TRUE
9395 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.12 | TRUE | TRUE
9396 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.12 | FALSE | TRUE
9398 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.13 | TRUE | TRUE
9399 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.13 | TRUE | TRUE
9400 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.13 | FALSE | TRUE
9402 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.14 | TRUE | TRUE
9403 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.14 | TRUE | TRUE
9404 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.14 | FALSE | TRUE
9406 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellV | Cell terminal voltage. | uint16 | lithium-ion-module-cell.15 | TRUE | TRUE
9407 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellTmp | Cell temperature. | int16 | lithium-ion-module-cell.15 | TRUE | TRUE
9408 | lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | Status of the cell. | bitfield32 | lithium-ion-module-cell.15 | FALSE | TRUE
9410 | end | End | ID | Model identifier | uint16 |  | TRUE | TRUE
9411 | end | End | L | Model length | uint16 |  | TRUE | TRUE

## Bitfields and Enums
Model | Model Label | Name | Type | Bit Name | Bit Number | Description | Mandatory | Note
battery | Battery Base Model | LocRemCtl | enum16 | REMOTE | 0 | Battery control mode: Controlled remotely | TRUE
battery | Battery Base Model | LocRemCtl | enum16 | LOCAL | 1 | Battery control mode: Controlled locally | TRUE
battery | Battery Base Model | Typ | enum16 | NOT_APPLICABLE_UNKNOWN | 0 | Type of battery: Not applicable or Unknown | TRUE
battery | Battery Base Model | Typ | enum16 | LEAD_ACID | 1 | Type of battery: Lead Acid | TRUE
battery | Battery Base Model | Typ | enum16 | NICKEL_METAL_HYDRATE | 2 | Type of battery: Nickel Metal Hydrate | TRUE
battery | Battery Base Model | Typ | enum16 | NICKEL_CADMIUM | 3 | Type of battery: Nickel Cadmium | TRUE
battery | Battery Base Model | Typ | enum16 | LITHIUM_ION | 4 | Type of battery: Lithium Ion | TRUE
battery | Battery Base Model | Typ | enum16 | CARBON_ZINC | 5 | Type of battery: Carbon Zinc | TRUE
battery | Battery Base Model | Typ | enum16 | ZINC_CHLORIDE | 6 | Type of battery: Zinc Chloride | TRUE
battery | Battery Base Model | Typ | enum16 | ALKALINE | 7 | Type of battery: Alkaline | TRUE
battery | Battery Base Model | Typ | enum16 | RECHARGEABLE_ALKALINE | 8 | Type of battery: Rechargeable Alkaline | TRUE
battery | Battery Base Model | Typ | enum16 | SODIUM_SULFUR | 9 | Type of battery: Sodium Sulfur | TRUE
battery | Battery Base Model | Typ | enum16 | FLOW | 10 | Type of battery: Flow | TRUE
battery | Battery Base Model | Typ | enum16 | OTHER | 99 | Type of battery: Other | TRUE
battery | Battery Base Model | State | enum16 | DISCONNECTED | 1 | State of the battery bank: Disconnected | TRUE
battery | Battery Base Model | State | enum16 | INITIALIZING | 2 | State of the battery bank: Initializing | TRUE
battery | Battery Base Model | State | enum16 | CONNECTED | 3 | State of the battery bank: Connected | TRUE
battery | Battery Base Model | State | enum16 | FAULTED | 99 | State of the battery bank: Faulted | TRUE
battery | Battery Base Model | Evt1 | bitfield32 | CURRENT_IMBALANCE_WARNING | 24 | Alarms and warnings: Current imbalance warning | TRUE
battery | Battery Base Model | Evt1 | bitfield32 | OTHER_ALARM | 25 | Alarms and warnings: Other faults | TRUE
battery | Battery Base Model | Evt1 | bitfield32 | OTHER_WARNING | 26 | Alarms and warnings: Other warnings | TRUE
battery | Battery Base Model | Evt1 | bitfield32 | CONFIGURATION_ALARM | 28 | Alarms and warnings: Configuration fault | TRUE
battery | Battery Base Model | Evt2 | bitfield32 | - | - | Alarms and warnings: Not used, set to 0. | TRUE | Unused
battery | Battery Base Model | EvtVnd1 | bitfield32 | control_watchdog | 0 | Vendor defined faults: Control watchdog | TRUE
battery | Battery Base Model | EvtVnd1 | bitfield32 | config_fault | 1 | Vendor defined faults: MSC configuration | TRUE
battery | Battery Base Model | EvtVnd1 | bitfield32 | stack_config_fault | 2 | Vendor defined faults: Stack configuration | TRUE
battery | Battery Base Model | EvtVnd1 | bitfield32 | current_imbalance | 3 | Vendor defined faults: Current imbalance | TRUE
battery | Battery Base Model | EvtVnd1 | bitfield32 | stacks_ready | 4 | Vendor defined faults: Stacks ready | TRUE
battery | Battery Base Model | EvtVnd1 | bitfield32 | invalid_configurable_registers | 5 | Vendor defined faults: Invalid configurable register name entered in configuration | TRUE
battery | Battery Base Model | EvtVnd2 | bitfield32 | stacks_warning | 0 | Vendor defined warnings: Stack warning | TRUE
battery | Battery Base Model | EvtVnd2 | bitfield32 | control_watchdog | 1 | Vendor defined warnings: Control watchdog | TRUE
battery | Battery Base Model | EvtVnd2 | bitfield32 | current_imbalance | 2 | Vendor defined warnings: Current imbalance | TRUE
battery | Battery Base Model | EvtVnd2 | bitfield32 | stacks_ready | 3 | Vendor defined warnings: Stacks ready | TRUE
battery | Battery Base Model | EvtVnd2 | bitfield32 | stacks_bms_version | 4 | Vendor defined warnings: Incompatible stack BMS version | TRUE
battery | Battery Base Model | EvtVnd2 | bitfield32 | invalid_configurable_registers | 5 | Vendor defined warnings: Invalid configurable register name entered in configuration | TRUE
battery | Battery Base Model | SetOp | enum16 | CONNECT | 1 | Connect battery stack | TRUE
battery | Battery Base Model | SetOp | enum16 | DISCONNECT | 2 | Disconnect battery stack | TRUE
battery | Battery Base Model | SetInvState | enum16 | INVERTER_STOPPED | 1 | Set inverter state to stopped | TRUE | Unused
battery | Battery Base Model | SetInvState | enum16 | INVERTER_STANDBY | 2 | Set inverter state to standby | TRUE | Unused
battery | Battery Base Model | SetInvState | enum16 | INVERTER_STARTED | 3 | Set inverter state to started | TRUE | Unused
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSt | bitfield32 | STRING_ENABLED | 0 | Current status of the string: Enabled | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSt | bitfield32 | CONTACTOR_STATUS | 1 | Current status of the string: Contactor Status | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | COMMUNICATION_ERROR | 0 | Stack warnings and faults: Communication error | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | OVER_TEMP_ALARM | 1 | Stack warnings and faults: Over temperature fault | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | OVER_TEMP_WARNING | 2 | Stack warnings and faults: Over temperature warning | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | UNDER_TEMP_ALARM | 3 | Stack warnings and faults: Under temperature fault | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | UNDER_TEMP_WARNING | 4 | Stack warnings and faults: Under temperature warning | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | OVER_CHARGE_CURRENT_ALARM | 5 | Stack warnings and faults: Over charge current fault | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | OVER_CHARGE_CURRENT_WARNING | 6 | Stack warnings and faults: Over charge current warning | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | OVER_DISCHARGE_CURRENT_ALARM | 7 | Stack warnings and faults: Over discharge current fault | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | OVER_DISCHARGE_CURRENT_WARNING | 8 | Stack warnings and faults: Over discharge current warning | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | OVER_VOLT_ALARM | 9 | Stack warnings and faults: Over voltage fault | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | OVER_VOLT_WARNING | 10 | Stack warnings and faults: Over voltage warning | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | UNDER_VOLT_ALARM | 11 | Stack warnings and faults: Under voltage fault | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | UNDER_VOLT_WARNING | 12 | Stack warnings and faults: Under voltage warning | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | VOLTAGE_IMBALANCE_WARNING | 17 | Stack warnings and faults: Voltage imbalance warning | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | CONTACTOR_ERROR | 20 | Stack warnings and faults: Contactor error | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | FAN_ERROR | 21 | Stack warnings and faults: Fan error | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | GROUND_FAULT | 22 | Stack warnings and faults: Ground fault | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | OPEN_DOOR_ERROR | 23 | Stack warnings and faults: Open door error | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | OTHER_ALARM | 25 | Stack warnings and faults: Other faults | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | OTHER_WARNING | 26 | Stack warnings and faults: Other warnings | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | CONFIGURATION_ALARM | 28 | Stack warnings and faults: Configuration fault | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrEvt1 | bitfield32 | CONFIGURATION_WARNING | 29 | Stack warnings and faults: Configuration warning | TRUE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetEna | enum16 | ENABLE_STRING | 1 | Enables the string | FALSE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetEna | enum16 | DISABLE_STRING | 2 | Disables the string | FALSE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetCon | enum16 | CONNECT_STRING | 1 | Connects the string | FALSE
lithium_ion_bank | Lithium-Ion Battery Bank Model | string.StrSetCon | enum16 | DISCONNECT_STRING | 2 | Disconnects the string | FALSE
lithium_ion_string | Lithium-Ion String Model | St | bitfield32 | STRING_ENABLED | 0 | Current status of the string: Enabled | TRUE
lithium_ion_string | Lithium-Ion String Model | St | bitfield32 | CONTACTOR_STATUS | 1 | Current status of the string: Contactor Status | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | COMMUNICATION_ERROR | 0 | Stack warnings and faults: Communication error | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | OVER_TEMP_ALARM | 1 | Stack warnings and faults: Over temperature fault | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | OVER_TEMP_WARNING | 2 | Stack warnings and faults: Over temperature warning | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | UNDER_TEMP_ALARM | 3 | Stack warnings and faults: Under temperature fault | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | UNDER_TEMP_WARNING | 4 | Stack warnings and faults: Under temperature warning | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | OVER_CHARGE_CURRENT_ALARM | 5 | Stack warnings and faults: Over charge current fault | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | OVER_CHARGE_CURRENT_WARNING | 6 | Stack warnings and faults: Over charge current warning | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | OVER_DISCHARGE_CURRENT_ALARM | 7 | Stack warnings and faults: Over discharge current fault | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | OVER_DISCHARGE_CURRENT_WARNING | 8 | Stack warnings and faults: Over discharge current warning | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | OVER_VOLT_ALARM | 9 | Stack warnings and faults: Over voltage fault | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | OVER_VOLT_WARNING | 10 | Stack warnings and faults: Over voltage warning | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | UNDER_VOLT_ALARM | 11 | Stack warnings and faults: Under voltage fault | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | UNDER_VOLT_WARNING | 12 | Stack warnings and faults: Under voltage warning | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | VOLTAGE_IMBALANCE_WARNING | 17 | Stack warnings and faults: Voltage imbalance warning | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | CONTACTOR_ERROR | 20 | Stack warnings and faults: Contactor error | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | FAN_ERROR | 21 | Stack warnings and faults: Fan error | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | GROUND_FAULT | 22 | Stack warnings and faults: Ground fault | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | OPEN_DOOR_ERROR | 23 | Stack warnings and faults: Open door error | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | OTHER_ALARM | 25 | Stack warnings and faults: Other faults | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | OTHER_WARNING | 26 | Stack warnings and faults: Other warnings | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | CONFIGURATION_ALARM | 28 | Stack warnings and faults: Configuration fault | TRUE
lithium_ion_string | Lithium-Ion String Model | Evt1 | bitfield32 | CONFIGURATION_WARNING | 29 | Stack warnings and faults: Configuration warning | TRUE
lithium-ion-module | Lithium-Ion Module Model | lithium-ion-module-cell.CellSt | bitfield32 | CELL_IS_BALANCING | 0 | Cell status: Cell is balancing | FALSE